## DAR Old (hidden)
| Project No. | Date
| Sheet No. | Computed by
Subject | Checked by | Approved by
DESIGN CALCULATION
SHEET
of

## DAR (hidden)
Design calculation sheet
Project no.: | Date: | Sheet no.: | 25 | 25 | Computed by:
Subject |  |  |  |  | Checked by:
Approved by:
of

## North Tower (B3 To S1)
Design calculation sheet
Project no: |  |  |  | Date: |  | Sheet no.: | 1 | 3 | Computed by:
Subject: |  | MAKKAH HILLS - NORTH TOWER | [6 empty] | Checked by:
|  | Domestic and Treated water Pumps Head - Lifting Stage 1 (From B3 To S1) | [6 empty] | Approved by:
Pipe Friction
|  | Horizontal Pipe Run |  |  |  |  | ft
|  | Vertical Pipe Run |  |  | 371 |  | ft
|  | Friction |  |  | 3 |  | ft/100ft
|  | Pipe Friction |  |  | 11.13 |  | ft
|  | Elbows, Tees, etc. |  |  | 35%
|  | Resulting Pipe Friction |  |  | 15.0255 |  | ft
Accessories Friction
|  | Type | Qty | Size [inch] | Friction
|  | Globe | 1 | 12 | 320 |  | ft
|  | Y-Type Strainer Flanged End | 1 | 8 | 150 |  | ft
|  | Swing Check | 1 | 8 | 80 |  | ft
|  | Gate | 4 | 8 | 9 |  | ft
[5 empty] | 586 |  | ft
|  | Friction |  |  | 3 |  | ft/100ft
|  | Resulting Accessories Friction |  |  | 17.58 |  | ft
Static Head
|  | Elevation |  |  | Static Head
|  | B3 To S1 |  |  | 371 |  | ft
|  | Resulting Static Head |  |  | 371 |  | ft
|  | Total Pressure drop |  |  | 403.6055 |  | ft
|  | Adding 20% Safey Factor |  |  | 410.1266 |  | ft
(for pipe friction and accessories)
|  | Pump Head |  | = | 410.1266 | ft | = | 125.0386 | m
|  |  |  | = | 12.2663 | bar
|  | Pump Flow |  | = | 1000 | Gpm | = | 63.1 | L/s
|  | Estimated Power |  | = | g | x | Q | x | H
[6 empty] | pump h | x | motor h
|  |  |  | = | 9810 | x | 0.0631 | x | 125.0386
[6 empty] | 0.8 | x | 0.8
|  |  |  | = | 120937.9177 | watt | = | 120.9379 | Kw
|  |  |  | = | 162.1152 | Hp
Note on F12: akady: From Chart at D=8" and Flow = 1000 Gpm Friction = 2 Ft/100 Ft we take it 3 Ft/100 Ft for safety
of

## Data
VALVE LOSSES IN EQUIVALENT FEET OF PIPE
Nominal Pipe Size (mm) | Globe | 60º-Y | 45º-Y | Angle | Gate | Swing Check | Y-Type Strainer Flanged End | Y-Type Strainer Screwed End
0.375 | 17 | 8 | 6 | 6 | 0.6 | 5 | - | -
0.5 | 18 | 9 | 7 | 7 | 0.7 | 6 | - | 3
0.75 | 22 | 11 | 9 | 9 | 0.9 | 8 | - | 4
1 | 29 | 15 | 12 | 12 | 1 | 10 | - | 5
1.25 | 38 | 20 | 15 | 15 | 1.5 | 14 | - | 9
1.5 | 43 | 24 | 18 | 18 | 1.8 | 16 | - | 10
2 | 55 | 30 | 24 | 24 | 2.3 | 20 | 27 | 14
2.5 | 69 | 35 | 29 | 29 | 2.8 | 25 | 28 | 20
3 | 84 | 43 | 35 | 35 | 3.2 | 30 | 42 | 40
3.5 | 100 | 50 | 41 | 41 | 4 | 35 | 48 | -
4 | 120 | 58 | 47 | 47 | 4.5 | 40 | 60 | -
5 | 140 | 71 | 58 | 58 | 6 | 50 | 80 | -
6 | 170 | 88 | 70 | 70 | 7 | 60 | 110 | -
8 | 220 | 115 | 85 | 85 | 9 | 80 | 150 | -
10 | 280 | 145 | 105 | 105 | 12 | 100 | 190 | -
12 | 320 | 165 | 130 | 130 | 13 | 120 | 250 | -
14 | 360 | 185 | 155 | 155 | 15 | 135 | - | -
16 | 410 | 210 | 180 | 180 | 17 | 150 | - | -
18 | 460 | 240 | 200 | 200 | 19 | 165 | - | -
20 | 520 | 275 | 235 | 235 | 22 | 200 | - | -
24 | 610 | 320 | 265 | 265 | 25 | 240 | - | -
VALVE LOSSES IN EQUIVALENT METER OF PIPE
Nominal Pipe Size (mm) | Globe | 60º-Y | 45º-Y | Angle | Gate | Swing Check | Y-Type Strainer Flanged End | Y-Type Strainer Screwed End
10 | 5.1829 | 2.439 | 1.8293 | 1.8293 | 0.18293 | 1.5244 | - | -
15 | 5.4878 | 2.7439 | 2.1341 | 2.1341 | 0.21341 | 1.8293 | - | 0.91463
20 | 6.7073 | 3.3537 | 2.7439 | 2.7439 | 0.27439 | 2.439 | - | 1.2195
25 | 8.8415 | 4.5732 | 3.6585 | 3.6585 | 0.30488 | 3.0488 | - | 1.5244
32 | 11.5854 | 6.0976 | 4.5732 | 4.5732 | 0.45732 | 4.2683 | - | 2.7439
40 | 13.1098 | 7.3171 | 5.4878 | 5.4878 | 0.54878 | 4.878 | - | 3.0488
50 | 16.7683 | 9.1463 | 7.3171 | 7.3171 | 0.70122 | 6.0976 | 8.2317 | 4.2683
65 | 21.0366 | 10.6707 | 8.8415 | 8.8415 | 0.85366 | 7.622 | 8.5366 | 6.0976
80 | 25.6098 | 13.1098 | 10.6707 | 10.6707 | 0.97561 | 9.1463 | 12.8049 | 12.1951
90 | 30.4878 | 15.2439 | 12.5 | 12.5 | 1.2195 | 10.6707 | 14.6341 | -
100 | 36.5854 | 17.6829 | 14.3293 | 14.3293 | 1.372 | 12.1951 | 18.2927 | -
125 | 42.6829 | 21.6463 | 17.6829 | 17.6829 | 1.8293 | 15.2439 | 24.3902 | -
150 | 51.8293 | 26.8293 | 21.3415 | 21.3415 | 2.1341 | 18.2927 | 33.5366 | -
200 | 67.0732 | 35.061 | 25.9146 | 25.9146 | 2.7439 | 24.3902 | 45.7317 | -
250 | 85.3659 | 44.2073 | 32.0122 | 32.0122 | 3.6585 | 30.4878 | 57.9268 | -
300 | 97.561 | 50.3049 | 39.6341 | 39.6341 | 3.9634 | 36.5854 | 76.2195 | -
350 | 109.7561 | 56.4024 | 47.2561 | 47.2561 | 4.5732 | 41.1585 | - | -
400 | 125 | 64.0244 | 54.878 | 54.878 | 5.1829 | 45.7317 | - | -
450 | 140.2439 | 73.1707 | 60.9756 | 60.9756 | 5.7927 | 50.3049 | - | -
500 | 158.5366 | 83.8415 | 71.6463 | 71.6463 | 6.7073 | 60.9756 | - | -
600 | 185.9756 | 97.561 | 80.7927 | 80.7927 | 7.622 | 73.1707 | - | -

## BLANK
Design calculation sheet
Project no: |  | Date: | Sheet no.: | Computed by: | A.F.K
Subject: |  |  |  | Checked by:
Approved by:
of