## Dialog_bstr_exp_DATA (hidden)
Tank Data
OK
Cancel
Building
Floor
Tank No.
Axes

## Dialog_sump_pit_data (hidden)
Sump Pit Data
OK
Cancel
Building
Floor
Axes
Submersible Pump No.

## Dialog_Select_HFBS_Description (hidden)
Pipe Description
Select the pipe description from the following choices
Stack In More Than 3 Stories Building (S>3ST)
Main Horizontal Branch In More Than 3 Stories Building (MHB>3ST)

## Dialog_Select_BDS_Slope (hidden)
Pipe Slope
1% (1:100 or 1/8 inch/100ft)
Select the pipe slope from the following choices
0.5% (1:200 or 1/16 inch/100ft)
2% (1:50 or 1/4 inch/100ft)
4% (1:25 or 1/2 inch/100ft)

## Dialog_Select_WASTE_PIPE_TYPE (hidden)
Type of Waste Drainage pipe
Horizontal Fixture Branches And Stacks (HFBS)
Select the type of this waste drainage pipe from the following choices
Building Drains And Sewers (BDS)

## Dialog_Select_RW_Drain_Type (hidden)
Type of Rain Water Drain
Horizontal Pipe
Select the type of this drain from the following choices
Roof Drain
Storm Stack

## Dialog_option_sump_pit (hidden)
Options
Cancel
Delete Sump Pit
Open Sump Pit
Save Sump Pit
List of Saved Sump Pits
Reset

## Dialog_option_fuel_pipes (hidden)
Options
Cancel
Delete Network
Open Network
Save Network
List of Saved Fuel Networks
Reset All

## Dialog_fuel_pipes_data (hidden)
Network Data
OK
Cancel
Building
Floor
Network Code

## Dialog_vacuum_pipes_data (hidden)
Network Data
OK
Cancel
Building
Floor
Network Code

## Dialog_option_vacuum_pipes (hidden)
Options
Cancel
Delete Network
Open Network
Save Network
List of Saved Vacuum Air Networks
Reset

## Dialog_option_comp_air_pipes (hidden)
Options
Cancel
Delete Network
Open Network
Save Network
List of Saved Compressed Air Networks
Reset

## Dialog_comp_air_pipes_data (hidden)
Network Data
OK
Cancel
Building
Floor
Network Code

## Dialog_hwr_pipes_data (hidden)
Network Data
OK
Cancel
Building
Floor
Network Code

## Dialog_cw_hw_pipes_data_ (hidden)
Network Data
OK
Cancel
Building
Floor
Network Code

## Dialog_option_vent_pipes_ (hidden)
Options
Cancel
Delete Network
Open Network
Save Network
List of Saved Vent Drainage Networks
Reset All

## Dialog_vent_pipes_data_ (hidden)
Network Data
OK
Cancel
Building
Floor
Network Code

## Dialog_option_WASTE_pipeS_ (hidden)
Options
Cancel
Delete Network
Open Network
Save Network
List of Saved Waste Drainage Networks
Reset All

## Dialog_waste_pipes_data_ (hidden)
Network Data
OK
Cancel
Building
Floor
Network Code

## Dialog_RW_pipes_data (hidden)
Network Data
OK
Cancel
Building
Floor
Network Code

## Dialog_SUBMERSIBLE_HEAD_data (hidden)
Pump Data
OK
Cancel
Building
Floor
Axes
Pump No.

## Dialog_SUBMERSIBLE_DISCH_data (hidden)
Pump Data
OK
Cancel
Building
Floor
Axes
Pump No.

## Dialog_CIRCULATING_data (hidden)
Pump Data
OK
Cancel
Building
Floor
Axes
Pump No.

## Dialog_booster_head_data (hidden)
Pump Data
OK
Cancel
Building
Floor
Axes
Pump No.

## Dialog_option_submersible_disch (hidden)
Options
Cancel
Delete Pump
Open Pump
Save Pump
List of Saved Submersible Drainage Pump Discharges
Reset

## Dialog_option_SUBMERSIBLE_HEAD (hidden)
Options
Cancel
Delete Pump
Open Pump
Save Pump
List of Saved Submersible Drainage Pump Heads
Reset All

## Dialog_option_hwr_pipes (hidden)
Options
Cancel
Delete Network
Open Network
Save Network
List of Saved Hot Water Return Networks
Reset

## Dialog_option_cw_hw_pipes_ (hidden)
Options
Cancel
Delete Network
Open Network
Save Network
List of Saved Water Networks
Reset All

## Dialog_option_rw_pipes (hidden)
Options
Cancel
Delete Network
Open Network
Save Network
List of Saved Rain Water Drainage Networks
Reset

## Dialog_option_bstr_exp (hidden)
Options
Cancel
Delete Tank
Open Tank
Save Tank
List of Saved Booster Expansion Tanks
Reset

## Dialog_option_circulating (hidden)
Options
Cancel
Delete Pump
Open Pump
Save Pump
List of Saved Hot Water Circulating Pumps
Reset All

## Dialog_option_booster_Head (hidden)
Options
Cancel
Delete Pump
Open Pump
Save Pump
List of Saved Booster Pump Set Heads
Reset All

## BOOSTER PUMP SET HEAD (hidden)
[26 empty] | 1 |  |  |  |  | STEEL SHCEDULE 40 | 5 |  |  |  | TABLE 5-10-1 EQUIVALENT PIPE LENGTH (PAGE 14-17 IN NFPA-14)
| Booster Pump Set Head | [29 empty] | COPPER TYPE M | [6 empty] | 45O ELBOW | 90O ELBOW | 90O L TURN ELBOW | TEE | BUTTER-FLY VALVE | GATE VALVE | SWING CHECK VALVE | GLOBE VALVE | ANGLE VALVE
[19 empty] | Pipe Material |  |  |  | UNITS | [7 empty] | COPPER TYPE L |  |  |  |  | 0 | 0.5 | 0.76533 | 1.64 | 1.0933 | 3.28 | 2.1867 | 0.38267 | 4.5373 | 18.204 | 9.1293
[23 empty] | CATEGORY | FACTOR | INVERSE FACTOR | LINKCELL | CHANGE CELL |  |  |  | COPPER TYPE K |  |  |  |  | 0 | 0.75 | 0.9184 | 1.968 | 1.312 | 3.936 | 2.624 | 0.4592 | 5.4448 | 21.8448 | 10.9552
Height from The Pump Discharge Pipe Level to The Highest Sanitary Fixture | [20 empty] | Ft |  | PRESSURE | 14.5 | 1 | 2 | 2 |  |  |  | Polypropylene PN20 |  |  |  |  | 0 | 1 | 1.2245 | 2.624 | 1.7493 | 5.248 | 3.4987 | 0.61227 | 7.2597 | 29.1264 | 14.6069
Biggest Residual Pressure for The Highest Sanitary Fixture | [20 empty] | Psi |  | DISCHARGE | 15.85 | 1 | [5 empty] | 136 |  |  |  |  | 0 | 1.25 | 1.6837 | 3.608 | 2.4053 | 7.216 | 4.8107 | 0.84187 | 9.9821 | 40.0488 | 20.0845
Additional Pressure Losses | [17 empty] | 0 |  |  | Psi |  | LENGTH | 3.28 | 1 | [10 empty] | 0 | 1.5 | 1.9899 | 4.264 | 2.8427 | 8.528 | 5.6853 | 0.99493 | 11.7971 | 47.3304 | 23.7363
Losses in Pipes And Fittings | [17 empty] | 0 |  |  | Psi | [14 empty] | 0 | 2 | 2.6021 | 5.576 | 3.7173 | 11.152 | 7.4347 | 1.3011 | 15.4269 | 61.8936 | 31.0397
Pump Head | [17 empty] | 0 |  |  | Psi |  |  |  |  | STEEL | COPPER TYPE M | COPPER TYPE L | COPPER TYPE K | POLYPROPYLENE PN20 | [5 empty] | 0 | 2.5 | 3.0613 | 6.56 | 4.3733 | 13.12 | 8.7467 | 1.5307 | 18.1493 | 72.816 | 36.5173
Pipe Losses in Different Pipe Segmants | [24 empty] | 1 | 0 | 0 | 0 | 0 | 0 |  | 1 |  |  |  | 0 | 3 | 3.8267 | 8.2 | 5.4667 | 16.4 | 10.9333 | 1.9133 | 22.6867 | 91.02 | 45.6467
Ser. No. | Pipe Code | Outside Dia |  | Pipe Discharge |  | Pipe Length |  | Quantity of Fittings on The Pipe | [8 empty] | Flow Velocity |  | Pipe Total Length |  | Pressure Drop |  |  |  | 0 | 0.622 | 0.569 | 0.545 | 0.527 | 0.653 | 25 |  | 16.6 | 4.2 | 25/16.6 | 0 | 3.5 | 4.2859 | 9.184 | 6.1227 | 18.368 | 12.2453 | 2.1429 | 25.4091 | 101.9424 | 51.1243
[8 empty] | 45O Elbow | 90O Elbow | 90O L Turn Elbow | Tee | Butter- fly Valve | Gate Valve | Swing Check Valve | Globe Valve | Angle Valve | [6 empty] | Pipe Diameter | Total Equivalent length (FT) | 0 | 0.824 | 0.811 | 0.785 | 0.745 | 0.835 | 32 |  | 21.2 | 5.4 | 32/21.2 | 0 | 4 | 4.8981 | 10.496 | 6.9973 | 20.992 | 13.9947 | 2.4491 | 29.0389 | 116.5056 | 58.4277
1 |  | 0 | mm |  | Gpm |  | Ft | [9 empty] | #VALUE! | Ft/s | #VALUE! | Ft | #VALUE! | Psi | #VALUE! | #VALUE! | 0 | 1.049 | 1.055 | 1.025 | 0.995 | 1.047 | 40 |  | 26.6 | 6.7 | 40/26.6 | 0 | 5 | 6.1227 | 13.12 | 8.7467 | 26.24 | 9 | 3.0613 | 36.2987 | 145.632 | 73.0347
[25 empty] | 0 | 3 | 1.291 | 1.265 | 1.245 | 1.315 | 50 |  | 33.4 | 8.3 | 50/33.4 | 0 | 6 | 7.0411 | 15.088 | 10.0587 | 30.176 | 10 | 3.5205 | 41.7435 | 167.4768 | 83.9899
[25 empty] | 0 | 1.61 | 1.527 | 1.505 | 1.481 | 1.653 | 63 |  | 42 | 10.5 | 63/42 | 0 | 8 | 8.8779 | 19.024 | 12.6827 | 38.048 | 12 | 4.4389 | 52.6331 | 211.1664 | 105.9003
[25 empty] | 0 | 2.067 | 2.009 | 1.985 | 1.959 | 1.969 | 75 |  | 50 | 12.5 | 75/50 | 0 | 10 | 10.8677 | 23.288 | 15.5253 | 46.576 | 19 | 5.4339 | 64.4301 | 258.4968 | 129.6365
[25 empty] | 0 | 2.469 | 2.495 | 2.465 | 2.435 | 2.362 | 90 |  | 60 | 15 | 90/60 | 0 | 12 | 12.8576 | 27.552 | 18.368 | 55.104 | 21 | 6.4288 | 76.2272 | 305.8272 | 153.3728
[25 empty] | 0 | 3.068 | 2.981 | 2.945 | 2.907 | 2.89 | 110 |  | 73.4 | 18.3 | 110/73.4
[25 empty] | 0 | 3.548 | 3.459 | 3.425 | 3.385 | 3.285 | 125 |  | 83.4 | 20.8 | 125/83.4
[25 empty] | 0 | 4.026 | 3.935 | 3.905 | 3.857 | 4.205 | 160 |  | 106.8 | 26.6 | 160/106.8
MAI PLUMBING CALCULATIONS | [12 empty] | Booster Pump Set Head | [11 empty] | 0 | 5.047 | 4.907 | 4.875 | 4.805
[25 empty] | 0 | 6.065 | 5.881 | 5.845 | 5.741
Project: | [12 empty] | Building: | [11 empty] | 0 | 7.981 | 7.785
Client: | [12 empty] | Floor: | [11 empty] | 0 | 10.02 |  |  |  | 0
Contractor: | [12 empty] | Axes: | [11 empty] | 0 | 12.09 |  |  |  | 0
Engineer: | [12 empty] | Pump No.: | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | Pipe Material: |  |  | Polypropylene Pn20 | [9 empty] | 0 | 0 | 0 | 0 | 1
Pipe Losses in Different Pipe Segmants | [25 empty] | 0 | 0 | 0 | 0 | 0 | 0
Ser. No. | Pipe Code | Outside Dia |  | Pipe Discharge |  | Pipe Length |  | Quantity of Fittings on The Pipe | [8 empty] | Flow Velocity |  | Pipe Total Length |  | Pressure Drop
| =proper("PIPE CODE") | [6 empty] | 45O Elbow | 90O Elbow | 90O L Turn Elbow | Tee | Butter- fly Valve | Gate Valve | Swing Check Valve | Globe Valve | Angle Valve
Add Pipe
Reset Data Entry Table
Pump Data
Print
Options
Back
Delete Pipe
Go To Discharge Calculations
Units
S.I
British

## AIR COMPRESSOR (hidden)
Air Compressor
NOT DONE YET
Back

## Dialog_booster_discharge_DATA (hidden)
Pump Data
OK
Cancel
Building
Floor
Pump No.
Axes

## BOOSTER PUMP SET DISCHARGE (hidden)
| Booster Pump Set Discharge | [14 empty] | RECOMMENDED SYSTEM SPLIT |  | TWO EQUAL PUMPS | TWO PUMP SYSTEM | 25%-55%-55% SPLIT | 25%-75%-75% SPLIT
[14 empty] | DEMAND CORRESPONDS TO TOTAL FIXTURE UNITS (LPS) |  | 2 EQUAL PUMPS | 1 | 0-0 | 0 | 0 | 0
1 | [13 empty] | 0 |  | 2 PUMPS |  |  | 0 | 0 | 0
[8 empty] | % Split | [5 empty] | N/A |  | 3 PUMPS W/ 25%-55%-55% SPLIT |  |  | 0 | 0 | 0
3 PUMPS W/ 25%-75%-75% SPLIT
| MAI PLUMBING CALCULATIONS | [6 empty] | Booster Pump Set Discharge
| Project: | [6 empty] | Building:
| Client: | [6 empty] | Floor:
| Contractor: | [6 empty] | Axes:
| Engineer: | [6 empty] | Pump No.:
[8 empty] | Demand Type: | Total Demand
[8 empty] | % Split: | 2 Equal Pumps
| Separate Demand |  | Total Fixture Units |  | Demand Corresponds to Total Fixture Units |  | Pump Demand |  | Demands for The Different Pumps |  | units
| 0 | Gpm | 0 | FU | 0 | Gpm |  | Gpm |  | Gpm | category | factor | INVERSE factor | linkcell | CHANGE CELL
[11 empty] | discharge | 15.85 | 1 | 2 | 2
Demand Weights of Fixtures in Fixture Units
| Fixture or Group |  |  |  | Occupancy |  | Type of Supply Control | Weight in Fixture Units | Quantity | Total Fixture Units
| Water Closet |  |  |  | Public |  | Flush Valve | 10 |  | 0
| Water Closet |  |  |  | Public |  | Flush Tank | 5 |  | 0
| Pedestal Urinal |  |  |  | Public |  | Flush Valve | 10 |  | 0
| Stall Or Wall Urinal |  |  |  | Public |  | Flush Valve | 5 |  | 0
| Stall Or Wall Urinal |  |  |  | Public |  | Flush Tank | 3 |  | 0
| Lavatory |  |  |  | Public |  | Faucet | 2 |  | 0
| Bathtub |  |  |  | Public |  | Faucet | 4 |  | 0
| Shower Head |  |  |  | Public |  | Mixing Valve | 4 |  | 0
| Service Sink |  |  |  | Office..,Etc |  | Faucet | 3 |  | 0
| Kitchen Sink |  |  |  | Hotel Or Restaurant |  | Faucet | 4 |  | 0
| Water Closet |  |  |  | Private |  | Flush Valve | 6 |  | 0
| Water Closet |  |  |  | Private |  | Flush Tank | 3 |  | 0
| Lavatory |  |  |  | Private |  | Faucet | 1 |  | 0
| Bathtub |  |  |  | Private |  | Faucet | 2 |  | 0
| Shower Head |  |  |  | Private |  | Mixing Valve | 2 |  | 0
| Bathroom Group |  |  |  | Private |  | Flush Valve for Closet | 8 |  | 0
| Bathroom Group |  |  |  | Private |  | Flush Tank for Closet | 6 |  | 0
| Separate Shower |  |  |  | Private |  | Mixing Valve | 2 |  | 0
| Kitchen Sink |  |  |  | Private |  | Faucet | 2 |  | 0
| Laundry Trays (1 To 3) |  |  |  | Private |  | Faucet | 3 |  | 0
| Combination Fixture |  |  |  | Private |  | Faucet | 3 |  | 0
| Miscellaneous |  |  |  | -- |  | -- | 0.25 |  | 0
| Miscellaneous |  |  |  | -- |  | -- | 0.5 |  | 0
| Miscellaneous |  |  |  | -- |  | -- | 1 |  | 0
| Miscellaneous |  |  |  | -- |  | -- | 2 |  | 0
Total Demand
Separate Cold Water Demand
Separate Hot Water Demand
Pump Data
Print
Options
Back
Demand Type
Go To Head Calculations
Units
S.I
British

## HOT WATER CIRCULATING PUMP (hidden)
[26 empty] | 1 |  |  |  |  | STEEL SHCEDULE 40 | 5 |  |  |  | TABLE 5-10-1 EQUIVALENT PIPE LENGTH (PAGE 14-17 IN NFPA-14)
| Hot Water Circulating Pump | [21 empty] | UNITS | [7 empty] | COPPER TYPE M | [6 empty] | 45O ELBOW | 90O ELBOW | 90O L TURN ELBOW | TEE | BUTTER-FLY VALVE | GATE VALVE | SWING CHECK VALVE | GLOBE VALVE | ANGLE VALVE
[19 empty] | Pipe Material |  |  |  | CATEGORY | FACTOR | INVERSE FACTOR | LINKCELL | CHANGE CELL |  |  |  | COPPER TYPE L |  |  |  |  | 0 | 0.5 | 0.76533 | 1.64 | 1.0933 | 3.28 | 2.1867 | 0.38267 | 4.5373 | 18.204 | 9.1293
[23 empty] | PRESSURE | 1 | 14.5 | 1 | 1 |  |  |  | COPPER TYPE K |  |  |  |  | 0 | 0.75 | 0.9184 | 1.968 | 1.312 | 3.936 | 2.624 | 0.4592 | 5.4448 | 21.8448 | 10.9552
Pipe Length | [20 empty] | m |  | DISCHARGE | 1 | 15.85 | [5 empty] | POLYPROPYLENE PN20 |  |  |  |  | 0 | 1 | 1.2245 | 2.624 | 1.7493 | 5.248 | 3.4987 | 0.61227 | 7.2597 | 29.1264 | 14.6069
Temp. Difference | [17 empty] | 10 |  |  | oC |  | LENGTH | 1 | 3.28 | [5 empty] | 136 |  |  |  |  | 0 | 1.25 | 1.6837 | 3.608 | 2.4053 | 7.216 | 4.8107 | 0.84187 | 9.9821 | 40.0488 | 20.0845
Additional Pressure Losses | [17 empty] | 0 |  |  | Bar |  | TEMP. DIFF. | 1 | 1.8 | [10 empty] | 0 | 1.5 | 1.9899 | 4.264 | 2.8427 | 8.528 | 5.6853 | 0.99493 | 11.7971 | 47.3304 | 23.7363
Disharge | [17 empty] | 0 |  |  | Lps | [14 empty] | 0 | 2 | 2.6021 | 5.576 | 3.7173 | 11.152 | 7.4347 | 1.3011 | 15.4269 | 61.8936 | 31.0397
Pump Head | [17 empty] | 0 |  |  | Bar |  |  |  |  | STEEL | COPPER TYPE M | COPPER TYPE L | COPPER TYPE K | POLYPROPYLENE PN20 | [5 empty] | 0 | 2.5 | 3.0613 | 6.56 | 4.3733 | 13.12 | 8.7467 | 1.5307 | 18.1493 | 72.816 | 36.5173
Pipe Losses in Different Pipe Segmants | [24 empty] | 1 | 0 | 0 | 0 | 0 | 0 |  | 1 |  |  |  | 0 | 3 | 3.8267 | 8.2 | 5.4667 | 16.4 | 10.9333 | 1.9133 | 22.6867 | 91.02 | 45.6467
Ser. No. | Pipe Code | Outside Dia |  | Pipe Discharge |  | Pipe Length |  | Quantity of Fittings on The Pipe | [8 empty] | Flow Velocity |  | Pipe Total Length |  | Pressure Drop |  |  |  | 0 | 0.622 | 0.569 | 0.545 | 0.527 | 0.653 | 25 |  | 16.6 | 4.2 | 25/16.6 | 0 | 3.5 | 4.2859 | 9.184 | 6.1227 | 18.368 | 12.2453 | 2.1429 | 25.4091 | 101.9424 | 51.1243
[8 empty] | 45O Elbow | 90O Elbow | 90O L Turn Elbow | Tee | Butter- fly Valve | Gate Valve | Swing Check Valve | Globe Valve | Angle Valve | [6 empty] | Pipe Diameter | Total Equivalent Length | 0 | 0.824 | 0.811 | 0.785 | 0.745 | 0.835 | 32 |  | 21.2 | 5.4 | 32/21.2 | 0 | 4 | 4.8981 | 10.496 | 6.9973 | 20.992 | 13.9947 | 2.4491 | 29.0389 | 116.5056 | 58.4277
1 |  | 0 | mm |  | Lps |  | m | [9 empty] | #VALUE! | m/s | #VALUE! | m | #VALUE! | Bar | #VALUE! | #VALUE! | 0 | 1.049 | 1.055 | 1.025 | 0.995 | 1.047 | 40 |  | 26.6 | 6.7 | 40/26.6 | 0 | 5 | 6.1227 | 13.12 | 8.7467 | 26.24 | 9 | 3.0613 | 36.2987 | 145.632 | 73.0347
[25 empty] | 0 | 1.38 | 1.291 | 1.265 | 1.245 | 1.315 | 50 |  | 33.4 | 8.3 | 50/33.4 | 0 | 6 | 7.0411 | 15.088 | 10.0587 | 30.176 | 10 | 3.5205 | 41.7435 | 167.4768 | 83.9899
[25 empty] | 0 | 1.61 | 1.527 | 1.505 | 1.481 | 1.653 | 63 |  | 42 | 10.5 | 63/42 | 0 | 8 | 8.8779 | 19.024 | 12.6827 | 38.048 | 12 | 4.4389 | 52.6331 | 211.1664 | 105.9003
[25 empty] | 0 | 2.067 | 2.009 | 1.985 | 1.959 | 1.969 | 75 |  | 50 | 12.5 | 75/50 | 0 | 10 | 10.8677 | 23.288 | 15.5253 | 46.576 | 19 | 5.4339 | 64.4301 | 258.4968 | 129.6365
[25 empty] | 0 | 2.469 | 2.495 | 2.465 | 2.435 | 2.362 | 90 |  | 60 | 15 | 90/60 | 0 | 12 | 12.8576 | 27.552 | 18.368 | 55.104 | 21 | 6.4288 | 76.2272 | 305.8272 | 153.3728
[25 empty] | 0 | 3.068 | 2.981 | 2.945 | 2.907 | 2.89 | 110 |  | 73.4 | 18.3 | 110/73.4
[25 empty] | 0 | 3.548 | 3.459 | 3.425 | 3.385 | 3.285 | 125 |  | 83.4 | 20.8 | 125/83.4
[25 empty] | 0 | 4.026 | 3.935 | 3.905 | 3.857 | 4.205 | 160 |  | 106.8 | 26.6 | 160/106.8
MAI PLUMBING CALCULATIONS | [12 empty] | Hot Water Circulating Pump | [11 empty] | 0 | 5.047 | 4.907 | 4.875 | 4.805
[25 empty] | 0 | 6.065 | 5.881 | 5.845 | 5.741
Project: | [12 empty] | Building: | [11 empty] | 0 | 7.981 | 7.785
Client: | [12 empty] | Floor: | [11 empty] | 0 | 10.02 |  |  |  | 0
Contractor: | [12 empty] | Axes: | [11 empty] | 0 | 12.09 |  |  |  | 0
Engineer: | [12 empty] | Pump No.: | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | Pipe Material: |  |  | Polypropylene Pn20 | [9 empty] | 0 | 0 | 0 | 0 | 1
Pipe Losses in Different Pipe Segmants | [25 empty] | 0 | 0 | 0 | 0 | 0 | 0
Ser. No. | Pipe Code | Outside Dia |  | Pipe Discharge |  | Pipe Length |  | Quantity of Fittings on The Pipe | [8 empty] | Flow Velocity |  | Pipe Total Length |  | Pressure Drop
| Pipe Code | [6 empty] | 45O Elbow | 90O Elbow | 90O L Turn Elbow | Tee | Butter- fly Valve | Gate Valve | Swing Check Valve | Globe Valve | Angle Valve
Note on W6: The default temp. difference is 20 oF (11.1 oC) as per ASHRAE.
Add Pipe
Reset Data Entry Table
Pump Data
Print
Options
Back
Delete Pipe
Units
S.I
British

## SUBMERSIBLE PUMP HEAD (hidden)
[26 empty] | 1 |  |  |  |  | STEEL SHCEDULE 40 | 1 | TABLE 5-10-1 EQUIVALENT PIPE LENGTH (PAGE 14-17 IN NFPA-14)
| Submersible Drainage Pump Head | [29 empty] | COPPER TYPE M |  |  |  | 45O ELBOW | 90O ELBOW | 90O L TURN ELBOW | TEE | BUTTER-FLY VALVE | GATE VALVE | SWING CHECK VALVE | GLOBE VALVE | ANGLE VALVE
[19 empty] | Pipe Material |  |  |  | UNITS | [7 empty] | COPPER TYPE L |  | 0 | 0.5 | 0.76533 | 1.64 | 1.0933 | 3.28 | 2.1867 | 0.38267 | 4.5373 | 18.204 | 9.1293
[23 empty] | CATEGORY | FACTOR | INVERSE FACTOR | LINKCELL | CHANGE CELL |  |  |  | COPPER TYPE K |  | 0 | 0.75 | 0.9184 | 1.968 | 1.312 | 3.936 | 2.624 | 0.4592 | 5.4448 | 21.8448 | 10.9552
[23 empty] | PRESSURE | 1 | 14.5 | 1 | 1 |  |  |  | PLASTIC SCHEDULE 80 |  | 0 | 1 | 1.2245 | 2.624 | 1.7493 | 5.248 | 3.4987 | 0.61227 | 7.2597 | 29.1264 | 14.6069
Height from The Pump Discharge Level to The Connection Point With The Gravity Line | [20 empty] | m |  | DISCHARGE | 1 | 15.85 | [5 empty] | 136 |  | 0 | 1.25 | 1.6837 | 3.608 | 2.4053 | 7.216 | 4.8107 | 0.84187 | 9.9821 | 40.0488 | 20.0845
Additional Pressure Losses | [20 empty] | Bar |  | LENGTH | 1 | 3.28 | [7 empty] | 0 | 1.5 | 1.9899 | 4.264 | 2.8427 | 8.528 | 5.6853 | 0.99493 | 11.7971 | 47.3304 | 23.7363
Losses in Pipes And Fittings | [17 empty] | 0 |  |  | Bar | [11 empty] | 0 | 2 | 2.6021 | 5.576 | 3.7173 | 11.152 | 7.4347 | 1.3011 | 15.4269 | 61.8936 | 31.0397
Pump Head | [17 empty] | 0 |  |  | Bar |  |  |  |  | STEEL | COPPER TYPE M | COPPER TYPE L | COPPER TYPE K | PLASTIC Shc. 80 |  |  | 0 | 2.5 | 3.0613 | 6.56 | 4.3733 | 13.12 | 8.7467 | 1.5307 | 18.1493 | 72.816 | 36.5173
Pipe Losses in Different Pipe Segmants | [24 empty] | 1 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 3 | 3.8267 | 8.2 | 5.4667 | 16.4 | 10.9333 | 1.9133 | 22.6867 | 91.02 | 45.6467
Ser. No. | Pipe Code | Pipe Diam. |  | Pipe Discharge |  | Pipe Length |  | Quantity of Fittings on The Pipe | [8 empty] | Flow Velocity |  | Pipe Total Length |  | Pressure Drop |  |  |  | 0 | 0.622 | 0.569 | 0.545 | 0.527 | 0.546 | 0.5 |  | 0 | 3.5 | 4.2859 | 9.184 | 6.1227 | 18.368 | 12.2453 | 2.1429 | 25.4091 | 101.9424 | 51.1243
[8 empty] | 45O Elbow | 90O Elbow | 90O L Turn Elbow | Tee | Butter- fly Valve | Gate Valve | Swing Check Valve | Globe Valve | Angle Valve | [6 empty] | Pipe Diameter | Total Equivalent Length | 0 | 0.824 | 0.811 | 0.785 | 0.745 | 0.742 | 0.75 |  | 0 | 4 | 4.8981 | 10.496 | 6.9973 | 20.992 | 13.9947 | 2.4491 | 29.0389 | 116.5056 | 58.4277
1 |  | 0 | Inch |  | Lps |  | m | [9 empty] | #VALUE! | m/s | #VALUE! | m | #VALUE! | Bar | #VALUE! | #VALUE! | 0 | 1.049 | 1.055 | 1.025 | 0.995 | 0.957 | 1 |  | 0 | 5 | 6.1227 | 13.12 | 8.7467 | 26.24 | 9 | 3.0613 | 36.2987 | 145.632 | 73.0347
[25 empty] | 0 | 1.38 | 1.291 | 1.265 | 1.245 | 1.278 | 1.25 |  | 0 | 6 | 7.0411 | 15.088 | 10.0587 | 30.176 | 10 | 3.5205 | 41.7435 | 167.4768 | 83.9899
[25 empty] | 0 | 1.61 | 1.527 | 1.505 | 1.481 | 1.5 | 1.5 |  | 0 | 8 | 8.8779 | 19.024 | 12.6827 | 38.048 | 12 | 4.4389 | 52.6331 | 211.1664 | 105.9003
[25 empty] | 0 | 2.067 | 2.009 | 1.985 | 1.959 | 1.939 | 2 |  | 0 | 10 | 10.8677 | 23.288 | 15.5253 | 46.576 | 19 | 5.4339 | 64.4301 | 258.4968 | 129.6365
[25 empty] | 0 | 2.469 | 2.495 | 2.465 | 2.435 | 2.35 | 2.5 |  | 0 | 12 | 12.8576 | 27.552 | 18.368 | 55.104 | 21 | 6.4288 | 76.2272 | 305.8272 | 153.3728
[25 empty] | 0 | 3.068 | 2.981 | 2.945 | 2.907 | 2.9 | 3
[25 empty] | 0 | 3.548 | 3.459 | 3.425 | 3.385 | 3.385 | 3.5
[25 empty] | 0 | 4.026 | 3.935 | 3.905 | 3.857 | 3.826 | 4
MAI PLUMBING CALCULATIONS | [12 empty] | Submersible Drainage Pump Head | [11 empty] | 0 | 5.047 | 4.907 | 4.875 | 4.805 | 4.805 | 5
[25 empty] | 0 | 6.065 | 5.881 | 5.845 | 5.741 | 5.7 | 6
Project: | [12 empty] | Building: | [11 empty] | 0 | 7.981 | 7.785 |  |  | 7.6 | 8
Client: | [12 empty] | Floor: | [11 empty] | 0 | 10.02 |  |  |  | 0 | 10
Contractor: | [12 empty] | Axes: | [11 empty] | 0 | 12.09 |  |  |  | 0 | 12
Engineer: | [12 empty] | Pump No.: |  | 1 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | Pipe Material: |  |  | Steel Shcedule 40 | [9 empty] | 1 | 0 | 0 | 0 | 0
Pipe Losses in Different Pipe Segmants | [25 empty] | 0 | 0 | 0 | 0 | 0 | 0
Ser. No. | Pipe Code | Pipe Diam. |  | Pipe Discharge |  | Pipe Length |  | Quantity of Fittings on The Pipe | [8 empty] | Flow Velocity |  | Pipe Total Length |  | Pressure Drop
| Pipe Code | [6 empty] | 45O Elbow | 90O Elbow | 90O L Turn Elbow | Tee | Butter- fly Valve | Gate Valve | Swing Check Valve | Globe Valve | Angle Valve
Add Pipe
Reset Data Entry Table
Pump Data
Print
Options
Back
Delete Pipe
Go To Discharge Calculations
Units
S.I
British

## VACUUM AIR PUMP (hidden)
Vacuum Air Pump
NOT DONE YET
Back

## GREASE INTERCEPTOR (hidden)
Grease Interceptor Sizing |  | STEEL | STEEL | 2
|  | STEEL | COPPER
NOT DONE YET
Back

## LINT INTERCEPTOR SIZING (hidden)
Lint Interceptor Sizing |  | STEEL | STEEL | 2
|  | STEEL | COPPER
NOT DONE YET
Back

## OIL INTERCEPTOR (hidden)
Oil Interceptor Sizing |  | STEEL | STEEL | 2
|  | STEEL | COPPER
NOT DONE YET
L
Back

## SUMP PIT (hidden)
Sump Pit Sizing
MAI PLUMBING CALCULATIONS | [7 empty] | Sump Pits
Project: | [7 empty] | Building:
Client: | [7 empty] | Floor:
Contractor: | [7 empty] | Axes:
Engineer: | [7 empty] | Submersible Pump No.:
Input Data | [13 empty] | units
Submersible Pump Discharge |  | Height Between The Top of The Slab & The Bottom of Lowest Drainage Pipe Drained to The Sump Pit |  | Minimum Time Between Two Successive Starts |  | Sump Pit Length |  | Sump Pit Width |  | Height Between The Bottom of Lowest Drainage Pipe & The switch on Level |  | Minimum Height of Water Required to Submerge The Pump Discharge Pipe |  | category | factor | INVERSE factor | linkcell | CHANGE CELL
3.1546 | Lps | 0.5 | m | 10 | Min. | 1.5 | m | 1.5 | m | 0.3 | m | 0.25 | m | discharge | 1 | 15.85 | 1 | 1
[14 empty] | LENGTH | 1 | 3.28
Output Data | [13 empty] | VOLUME | 1 | 35.2876
Minimum Storage Volume for The Sump Pit |  | Storage Height | [5 empty] | 0.5m
1.8927 | m3 | 0.84122 | m | [8 empty] | 1.89m
Results | [7 empty] | 0.3m
Sump Pit Height (The Height Between The Top of The Slab & The Concrete Level of The Pit) | [7 empty] | 0.84m
1.8912 |  | m
0.25m
1.5m X 1.5m
Note on B29: Discharge of one pump of the duplex pump set.
Note on G29: Time to evacuate the sump pit.
Switch On Level
Switch Off Level
Lowest drainage Pipe Bottom Level
Add Defaul Information for Sump Pit
Sump Pit Data
Print
Options
Back
Units
S.I
British

## NEUTRALIZING PIT (hidden)
Neutralizing Pit Sizing |  | STEEL | STEEL | 2
|  | STEEL | COPPER
NOT DONE YET
Back

## TANKS SIZING (hidden)
Tank Sizing
NOT DONE YET
Back

## dialog_About_MAI (hidden)
About MAI Plumbing Calculations
OK
MAI Plumbing Calculations Version 1.7 2014
After years of experience in plumbing design, Eng. Mohamed El-Mai introduces the MAI Plumbing Calculation sheets. MAI Plumbing Calculations is a software prepared according to a wide variety of reputable codes
(NPC, ASHRAE...). While reasonable care has been exercised in the preparation and testing of the program, the author disclaims any warranty, expressed or implied, as to the accuracy or reliability of the data or
In order to improve the plumbing engineering design performance, Eng. Mohamed El-Mai introduces software MAI Plumbing Calculations for all plumbing engineers.
For any technical support, please contact: Eng. Mohamed El-Mai Adress: 35Tersa St.-Haram-Giza-Egypt Tel: 00965 97277803 E-mail: mam_work@yahoo.com
You must accept these terms if you wish to use the software.
calculations contained therein. It is the sole responsibility of the user to validate the data and to determine whether the results of this program are accurate and suitable for any purpose.

## Dialog_add_delete_fuel_pipe (hidden)
Add/Modify/Delete Pipe
Add New Pipe
Cancel
Add Pipe Feeding Two Existing Pipes
Modify Pipe Feeding Two Existing Pipes
Delete pipe

## Dialog_add_delete_vacuum_pipe (hidden)
Add/Modify/Delete Pipe
Add New Pipe
Cancel
Add Pipe Feeding Two Existing Pipes
Modify Pipe Feeding Two Existing Pipes
Delete pipe

## Dialog_add_delete_comp_air_PIPe (hidden)
Add/Modify/Delete Pipe
Add New Pipe
Cancel
Add Pipe Feeding Two Existing Pipes
Modify Pipe Feeding Two Existing Pipes
Delete pipe

## Dialog_add_delete_hwr_PIPe (hidden)
Add/Modify/Delete Pipe
Add New Pipe
Cancel
Add Pipe Feeding Two Existing Pipes
Modify Pipe Feeding Two Existing Pipes
Delete pipe

## Dialog_add_delete_rw_PIPe (hidden)
Add/Modify/Delete Pipe
Add New Pipe
Cancel
Add Pipe Draining Two Existing Pipes
Modify Pipe Draining Two Existing Pipes
Delete pipe

## RAIN WATER DRAINAGE PIPES (hidden)
Rain Water Pipes Sizing | [14 empty] | 2 In./Hr | 3 |  | FROM TABLE 13.6.2 (B) IN NPC AND TABLE 13-6-2 IN NATIONAL STANDARD PLUMBING CODE (PHCC)(HORIZOTAL STORM DRAINS) | [20 empty] | FROM TABLE 13.6.1 A IN NPC AND ZURN CATALOGUES (SIZE OF VERTICAL LEADERS)
| 1 | [13 empty] | 3 In./Hr |  |  | DRAIN SIZE (INCH) | 1/16 INCH SLOPE, INCHES RAIN FALL (SLOPE 0.5%) |  |  |  |  | 1/8 INCH SLOPE, INCHES RAIN FALL (SLOPE 1%) |  |  |  |  | 1/4 INCH SLOPE, INCHES RAIN FALL (SLOPE 2%) |  |  |  |  | 1/2 INCH SLOPE, INCHES RAIN FALL (SLOPE 4%) |  |  |  |  | DIAM. OF LEADER (INCH). | NORMAL RATE OF RAINFALL (INCH)
[15 empty] | 4 In./Hr |  |  |  | 2 | 3 | 4 | 5 | 6 | 2 | 3 | 4 | 5 | 6 | 2 | 3 | 4 | 5 | 6 | 2 | 3 | 4 | 5 | 6 |  | 2 | 3 | 4 | 5 | 6
[11 empty] | Rain Fall |  |  |  | 5 In./Hr |  |  |  | 1/16 INCH SLOPE, INCHES RAIN FALL (SLOPE 0.5%) 2: SQUARE FEET OF ROOF AREA |  | SQUARE FEET OF ROOF AREA
[15 empty] | 6 In./Hr |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 2 | 1/4 INCH SLOPE, INCHES RAIN FALL (SLOPE 2%) 2: 816; 1/4 INCH SLOPE, INCHES RAIN FALL (SLOPE 2%) 3: 544; 1/4 INCH SLOPE, INCHES RAIN FALL (SLOPE 2%) 4: 408; 1/4 INCH SLOPE, INCHES RAIN FALL (SLOPE 2%) 5: 326; 1/4 INCH SLOPE, INCHES RAIN FALL (SLOPE 2%) 6: 272; 1/2 INCH SLOPE, INCHES RAIN FALL (SLOPE 4%) 2: 1152; 1/2 INCH SLOPE, INCHES RAIN FALL (SLOPE 4%) 3: 768; 1/2 INCH SLOPE, INCHES RAIN FALL (SLOPE 4%) 4: 576; 1/2 INCH SLOPE, INCHES RAIN FALL (SLOPE 4%) 5: 461; 1/2 INCH SLOPE, INCHES RAIN FALL (SLOPE 4%) 6: 384 | 2 | 1440 | 960 | 720 | 576 | 480
[18 empty] | 3 | [5 empty] | 1644 | 1096 | 822 | 657 | 548 | 2320 | 1546 | 1160 | 928 | 773 | 3290 | 2193 | 1644 | 1316 | 1100 | 2.5 | 2600 | 1733 | 1300 | 1040 | 865
Ser. No. | Pipe Code | Type of Drain | Area Projected to Rain Water |  | Drainage Fixture Units |  | Continuous Flow |  | Total Area |  | Pipe or Roof Drain Size |  | RD Size | Area Corresponds to DRAINAGE FIXTURE UNITS (ft2) | Area Corresponds to CONTINUOUS FLOW (ft2) | PIPE SIZE (INCH) | MSG BOX RAIN WATER DRAIN TYPE | 4 | [5 empty] | 3760 | 2506 | 1880 | 1504 | 1253 | 5300 | 3533 | 2650 | 2120 | 1766 | 7520 | 5013 | 3760 | 3008 | 2510 | 3 | 4400 | 2933 | 2200 | 1760 | 1470
1 |  | ROOF DRAIN |  | Ft2 |  | Dfu |  | Gpm | 0 | Ft2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! |  | 5 | 4800 | 3200 | 2400 | 1920 | 1600 | 6680 | 4453 | 3340 | 2672 | 2227 | 9440 | 6293 | 4720 | 3776 | 3146 | 13360 | 8910 | 6680 | 5344 | 4450 | 4 | 9200 | 6133 | 4600 | 3680 | 3070
[18 empty] | 6 | 7720 | 5140 | 3860 | 3088 | 2575 | 10700 | 7133 | 5350 | 4280 | 3566 | 15100 | 10066 | 7550 | 6040 | 5033 | 21400 | 14270 | 10700 | 8560 | 7130 | 5 | 17300 | 11530 | 8650 | 6920 | 5765
[18 empty] | 8 | 16360 | 10900 | 8180 | 6544 | 5450 | 23000 | 15333 | 11500 | 9200 | 7600 | 32600 | 21733 | 16300 | 13040 | 10866 | 46000 | 30660 | 23000 | 18400 | 15330 | 6 | 27000 | 18000 | 13500 | 10800 | 9000
[18 empty] | 10 | 29840 | 19870 | 14920 | 11936 | 9950 | 41400 | 27600 | 20700 | 16560 | 13800 | 58400 | 38930 | 29200 | 23360 | 19470 | 82800 | 55190 | 41400 | 33120 | 27600 | 8 | 58000 | 38660 | 29000 | 23200 | 19315
[15 empty] | Drain Type |  |  | 12 | 48000 | 31970 | 24000 | 19200 | 16000 | 66600 | 44400 | 33300 | 26640 | 22200 | 94000 | 62660 | 47000 | 37600 | 31335 | 133200 | 88800 | 66600 | 53280 | 44400
[15 empty] | HORIZONTAL PIPE | 2 |  | 15 | [5 empty] | 119000 | 79330 | 59500 | 47600 | 39670 | 168000 | 112000 | 84000 | 67200 | 56000 | 238000 | 158500 | 119000 | 95200 | 79330
ROOF DRAIN
STORM STACK
MAI PLUMBING CALCULATIONS | [7 empty] | Rain Water Drainage Pipes
Project: | [7 empty] | Building:
Client: | [7 empty] | Floor:
Contractor: | [7 empty] | Network Code:
Engineer: | [7 empty] | Pipe Slope (in/foot): |  | 1/16
[8 empty] | Rain Fall: | 4 In./Hr
Ser. No. | Pipe Code | Type of Drain | Area Projected to Rain Water |  | Drainage Fixture Units |  | Continuous Flow |  | Total Area |  | Pipe or Roof Drain Size
[18 empty] | units | 1/16 INCH SLOPE, INCHES RAIN FALL (SLOPE 0.5%) 2: 0
[18 empty] | category | 1/16 INCH SLOPE, INCHES RAIN FALL (SLOPE 0.5%) 2: factor; 1/16 INCH SLOPE, INCHES RAIN FALL (SLOPE 0.5%) 3: INVERSE factor; 1/16 INCH SLOPE, INCHES RAIN FALL (SLOPE 0.5%) 4: linkcell; 1/16 INCH SLOPE, INCHES RAIN FALL (SLOPE 0.5%) 5: CHANGE CELL
[18 empty] | Area | 1/16 INCH SLOPE, INCHES RAIN FALL (SLOPE 0.5%) 2: 10.7584; 1/16 INCH SLOPE, INCHES RAIN FALL (SLOPE 0.5%) 3: 1; 1/16 INCH SLOPE, INCHES RAIN FALL (SLOPE 0.5%) 4: 2; 1/16 INCH SLOPE, INCHES RAIN FALL (SLOPE 0.5%) 5: 2
[18 empty] | Discharge | 1/16 INCH SLOPE, INCHES RAIN FALL (SLOPE 0.5%) 2: 15.85; 1/16 INCH SLOPE, INCHES RAIN FALL (SLOPE 0.5%) 3: 1
Note on M4: Default RF for Egypt & Lebanon is 4 In/Hr
1/16 In./Foot (0.5 %) Pipe Slope
1/8 In./Foot (1 %) Pipe Slope
1/4 In./Foot (2 %) Pipe Slope
1/2 In./Foot (4 %) Pipe Slope
Network Data
Add/Modify/Delete Pipe
Print
Options
Back
Pipe Slope
Units
S.I
British

## Dialog_add_delete_vent_PIPe_ (hidden)
Add/Copy/Modify/Delete Pipe
Add New Pipe
Cancel
Copy Pipe
Add Pipe Venting Two Existing Pipes
Modify Pipe Venting Two Existing Pipes
Delete Pipe

## Dialog_add_delete_waste_PIPe_ (hidden)
Add/Copy/Modify/Delete Pipe
Add New Pipe
Cancel
Copy Pipe
Add Pipe Draining Two Existing Pipes
Modify Pipe Draining Two Existing Pipes
Delete Pipe

## WASTE DRAINAGE PIPES_ (hidden)
Waste Drainage Pipe Sizing
| 2 | [41 empty] | Pipe Description | [18 empty] | 2 | HORIZONTAL FIXTURE BRANCH (HB<3ST) | HB<3ST |  |  | HORIZONTAL FIXTURE BRANCH (HB<3ST) | 0.5 % Slope (1/16 In./Foot ) |  |  |  | *BDS: Building Drains And Sewers.
[63 empty] | STACK OF 3 STORIES OR INTERVALS (S<3ST) | S<3ST |  |  | STACK OF 3 STORIES OR INTERVALS (S<3ST) | 1 % Slope (1/8 In./Foot) |  |  |  | *HFBS: Horizontal Fixture Branch And Stack.
[63 empty] | STACK IN MORE THAN 3 STORIES BUILDING (S>3ST) | S>3ST |  |  | STACK IN MORE THAN 3 STORIES BUILDING (S>3ST) | 2 % Slope (1/4 In./Foot) |  |  |  | **HB<3ST: Horizontal Fixture Branch in 3 Stories (or less) Building
[63 empty] | MAIN HORIZONTAL BRANCH IN MORE THAN 3 STORIES BUILDING (MHB>3ST) | MHB>3ST |  |  | MAIN HORIZONTAL BRANCH IN MORE THAN 3 STORIES BUILDING (MHB>3ST) | 4 % Slope (1/2 In./Foot) |  |  |  | **S<3ST: Stack of 3 Intervals or 3 Stories (or less) Building
Ser. No. | Pipe Code | Continuous Flow |  | Area Projected to Rain Water |  | Quantity of Fixtures on The Pipe | [38 empty] | Drain Type* | Pipe Description** | Drainage Fixure Units Corresponds to Sanitary Fixtures |  | Total Drainage Fixtue Units |  | Pipe Size |  | DFU CORESSPONDS TO CONTINUOUS FLOW | DFU CORESSPONDS TO AREA PROJECTED TO RAIN WATER | PIPE SLOPE OR DESCRIPTION | PIPE SIZE | MSGBOX PIPE_ DESCRIPTION_ NOT_ENTERED | [14 empty] | **S>3ST: Stack in More Than 3 Stories Building
[6 empty] | Group (WC,Lav,Bath) F Tank | Group (WC,Lav,Bath) F Valve | Bathtub (W/ or Wout/ Shower) | Bathtub | Bidet | Combination Sink And Tray | Combination Sink W/Food Dispos. | Dental Unit or Cuspidor | Dental Lavatory | Drinking Fountain | Dishwasher Domestic | Floor Drain | Kitchen Sink Domestic | Kitchen Sink W/ Food Dispos. | Lavatory (Small P.O.) | Lavatory (Large P.O.) | Lavatory, Barber, Beauty Parlor | Lavatory, Surgeon'S | Laundry Tray (1 or 2 Comparts) | Shower Stall, Domestic | Showers ( Group) Per Head | Surgeons Sink | Flushing Rim Sink (W/ Valve) | Service Sink (Trap Standard) | Service Sink ( P Trap) | Pot Sink, Scullery Sink…Etc | Urinal,Pedestal,Siphon Jet,Blowout | Urinal, Wall Lip | Urinal Stall, Washout | Urinal Trough (Each 2 Feet Section) | Wash Sink, Each Set of Faucets | Water Closet (Tank Operated) | Water Closet (Valve Operated) | Fixture Drain or Trap Size 1 1/4 Inch | Fixture Drain or Trap Size 1 1/2 Inch | Fixture Drain or Trap Size 2 Inch | Fixture Drain or Trap Size 2 1/2 Inch | Fixture Drain or Trap Size 3 Inch | Fixture Drain or Trap Size 4 Inch | [27 empty] | **MHB>3ST: Main Horizontal Branch in More Than 3 Stories Building
[6 empty] | 6 | 8 | 2 | 3 | 3 | 3 | 4 | 1 | 1 | 0.5 | 2 | 1 | 2 | 3 | 1 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 8 | 3 | 2 | 4 | 8 | 4 | 4 | 2 | 2 | 4 | 8 | 1 | 2 | 3 | 4 | 5 | 6
1 |  |  | Lps |  | m2 | [39 empty] | HFBS | S<3ST | 0 | Dfu | 0 | Dfu | #VALUE! | #VALUE! | 0 | 0 | 2 | #VALUE! | #VALUE! | HB<3ST | S<3ST | S>3ST | MHB>3ST |  | TABLE 11.5.2 IN NPC (BUILDING DRAINS AND SEWERS) |  |  |  |  | TABLE 11.5.3 IN NPC (HORIZONTAL FIXTURE BRANCHES AND STACKS)
[63 empty] | DIAM. OF PIPE (INCH) | MAXIMUM NUMBER OF FIXTURE UNITS THAT MAY BE CONNECTED TO ANY PORTION OF THE BUILDING DRAIN OR THE BUIDING SEWER |  |  |  | MAXIMUM NUMBER OF FIXTURE UNITS THAT MAY BE CONNECTED TO:
[64 empty] | FALL PER FOOT (SLOPE) |  |  |  | HORIZONTAL FIXTURE BRANCH | STACK OF 3 STORIES OR INTERVALS | MORE THAN 3 STORIES IN HEIGHT
[64 empty] | 1/16 IN. (0.5%) | 1/8 IN. (1%) | 1/4 IN. (2%) | 1/2 IN. (4%) |  |  | TOTAL FOR STACK | TOTAL AT ONE MAIN HORIZONTAL BRANCH
[64 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1 |  |  |  |  | 1 | 2 | 2 | 1
[63 empty] | 1.5 |  |  |  |  | 3 | 4 | 8 | 2
[63 empty] | 2 |  |  | 21 | 26 | 6 | 10 | 24 | 6
[63 empty] | 2.5 |  |  | 24 | 31 | 12 | 20 | 42 | 9
[63 empty] | 3 |  | 20 | 27 | 36 | 20 | 30 | 60 | 16
[63 empty] | 4 |  | 180 | 216 | 250 | 160 | 240 | 500 | 90
[63 empty] | 5 |  | 390 | 480 | 575 | 360 | 540 | 1100 | 200
MAI PLUMBING CALCULATIONS | [32 empty] | Waste Water Drainage Pipes | [29 empty] | 6 |  | 700 | 840 | 1000 | 620 | 960 | 1900 | 350
[63 empty] | 8 | 1400 | 1600 | 1920 | 2300 | 1400 | 2200 | 3600 | 600
Project: | [32 empty] | Building: | [29 empty] | 10 | 2500 | 2900 | 3500 | 4200 | 2500 | 3800 | 5600 | 1000
Client: | [32 empty] | Floor: | [29 empty] | 12 | 3900 | 4600 | 5600 | 6700 | 3900 | 6000 | 8400 | 1500
Contractor: | [32 empty] | Network Code: | [29 empty] | 15 | 7000 | 8300 | 10000 | 12000 | 7000
Engineer: | [54 empty] | BDS |  | HFBS
BDS
Ser. No. | Pipe Code | Continuous Flow |  | Area Projected to Rain Water |  | Quantity of Fixtures on The Pipe | [38 empty] | Drain Type* | Pipe Description** | Drainage Fixure Units Corresponds to Sanitary Fixtures |  | Total Drainage Fixtue Units |  | Pipe Size | [5 empty] | HFBS
[6 empty] | Group (WC,Lav,Bath) F Tank | Group (WC,Lav,Bath) F Valve | Bathtub (W/ or Wout/ Shower) | Bathtub | Bidet | Combination Sink And Tray | Combination Sink W/Food Disposal | Dental Unit or Cuspidor | Dental Lavatory | Drinking Fountain | Dishwasher Domestic | Floor Drain | Kitchen Sink Domestic | Kitchen Sink W/ Food Disposal | Lavatory (Small P.O.) | Lavatory (Large P.O.) | Lavatory, Barber, Beauty Parlor | Lavatory, Surgeon'S | Laundry Tray (1 or 2 Comparts.) | Shower Stall, Domestic | Showers ( Group) Per Head | Surgeons Sink | Flushing Rim Sink (W/ Valve) | Service Sink (Trap Standard) | Service Sink ( P Trap) | Pot Sink, Scullery Sink…Etc | Urinal, Pedestal, Siphon Jet, Blowout | Urinal, Wall Lip | Urinal Stall, Washout | Urinal Trough (Each 2 Feet Section) | Wash Sink, Each Set of Faucets | Water Closet (Tank Operated) | Water Closet (Valve Operated) | Fixture Drain or Trap Size 1 1/4 Inch | Fixture Drain or Trap Size 1 1/2 Inch | Fixture Drain or Trap Size 2 Inch | Fixture Drain or Trap Size 2 1/2 Inch | Fixture Drain or Trap Size 3 Inch | Fixture Drain or Trap Size 4 Inch
[6 empty] | 6 | 8 | 2 | 3 | 3 | 3 | 4 | 1 | 1 | 0.5 | 2 | 1 | 2 | 3 | 1 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 8 | 3 | 2 | 4 | 8 | 4 | 4 | 2 | 2 | 4 | 8 | 1 | 2 | 3 | 4 | 5 | 6
[63 empty] | units | 0
[63 empty] | category | factor | INVERSE factor | linkcell | CHANGE CELL
[63 empty] | Area | 1 | 10.7584 | 1 | 1
[63 empty] | Discharge | 1 | 15.85
Building Drains And Sewers (BDS)
Horizontal Fixture Branches And Stacks (HFBS)
Reset Sanitary Fixtures Table
Network Data
Print
Options
Back
Drian Type
Normal View
Add/Copy/Modify/Delete Pipe
Units
S.I
British

## VENT PIPES_ (hidden)
Vent Pipe Sizing | [50 empty] | 1 | 1.25 | TABLE 12.21.5 IN NPC (SIZE AND LENGTH OF VENTS)
[52 empty] | 1.5 | SIZE OF SOIL OR WASTE STACK (INCH0 | FIXTURE UNITS CONNECTED |  | Diameter of Vent Required(inch)
[52 empty] | 2 |  |  |  | 1.25 | 1.5 | 2 | 2.5 | 3 | 4 | 5 | 6 | 8
[52 empty] | 2.5 |  |  |  | MAXIMUM LENGTH OF VENT (Ft)
[52 empty] | 3 |  | 0
Ser. No. | Pipe Code | Pipe Length |  | Size of Waste Stack or Header |  | Quantity of Fixtures on The Pipe | [38 empty] | Total Fixture Units |  | Pipe Size |  | PIPE SIZE | MSG BOX Increase Waste Stack Size |  | 4 | 1.25 | 2 | 0 | 30
[6 empty] | Group (WC,Lav,Bath) F Tank | Group (WC,Lav,Bath) F Valve | Bathtub (W/ or Wout/ Shower) | Bathtub | Bidet | Combination Sink And Tray | Combination Sink W/Food Disposal | Dental Unit or Cuspidor | Dental Lavatory | Drinking Fountain | Dishwasher Domestic | Floor Drain | Kitchen Sink Domestic | Kitchen Sink W/ Food Disposal | Lavatory (Small P.O.) | Lavatory (Large P.O.) | Lavatory, Barber, Beauty Parlor | Lavatory, Surgeon'S | Laundry Tray (1 or 2 Comparts.) | Shower Stall, Domestic | Showers ( Group) Per Head | Surgeons Sink | Flushing Rim Sink (W/ Valve) | Service Sink (Trap Standard) | Service Sink ( P Trap) | Pot Sink, Scullery Sink…Etc | Urinal, Pedestal, Siphon Jet, Blowout | Urinal, Wall Lip | Urinal Stall, Washout | Urinal Trough (Each 2 Feet Section) | Wash Sink, Each Set of Faucets | Water Closet (Tank Operated) | Water Closet (Valve Operated) | Fixture Drain or Trap Size 1 1/4 Inch | Fixture Drain or Trap Size 1 1/2 Inch | Fixture Drain or Trap Size 2 Inch | Fixture Drain or Trap Size 2 1/2 Inch | Fixture Drain or Trap Size 3 Inch | Fixture Drain or Trap Size 4 Inch | [7 empty] | 5 |  | 0
[6 empty] | 6 | 8 | 2 | 3 | 3 | 3 | 4 | 1 | 1 | 0.5 | 2 | 1 | 2 | 3 | 1 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 8 | 3 | 2 | 4 | 8 | 4 | 4 | 2 | 2 | 4 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | [7 empty] | 6 | 1.5 | 8 | 0 | 50 | 150
1 |  |  | Ft | 1.25 | In. | [39 empty] | 0 | Dfu |  | Inch | #VALUE! | #VALUE! |  | 8 | 1.5 | 10 | 0 | 30 | 100
[52 empty] | 10 |  | 0
[53 empty] | 2 | 12 | 0 | 30 | 75 | 200
[53 empty] | 2 | 20 | 0 | 26 | 50 | 150
0
[53 empty] | 2.5 | 42 | 0 |  | 30 | 100 | 300
0
[53 empty] | 3 | 10 | 0 |  | 30 | 100 | 200 | 600
[53 empty] | 3 | 30 | 0 |  |  | 60 | 200 | 500
[53 empty] | 3 | 60 | 0 |  |  | 50 | 80 | 400
0
[53 empty] | 4 | 100 | 0 |  |  | 35 | 100 | 260 | 1000
MAI PLUMBING CALCULATIONS | [32 empty] | Drainage Vent Pipes | [19 empty] | 4 | 200 | 0 |  |  | 30 | 90 | 250 | 900
[53 empty] | 4 | 500 | 0 |  |  | 20 | 70 | 180 | 700
Project: | [32 empty] | Building: | [20 empty] | 0
Client: | [32 empty] | Floor: | [19 empty] | 5 | 200 | 0 |  |  |  | 35 | 80 | 350 | 1000
Contractor: | [32 empty] | Network Code: | [19 empty] | 5 | 500 | 0 |  |  |  | 30 | 70 | 300 | 900
Engineer: | [52 empty] | 5 | 1100 | 0 |  |  |  | 20 | 50 | 200 | 700
0
Ser. No. | Pipe Code | Pipe Length |  | Size of Waste Stack or Header |  | Quantity of Fixtures on The pipe | [38 empty] | Total Fixture Units |  | Pipe Size | [5 empty] | 6 | 350 | 0 |  |  |  | 25 | 50 | 200 | 400 | 1300
[6 empty] | Group (WC,Lav,Bath) F Tank | Group (WC,Lav,Bath) F Valve | Bathtub (W/ or Wout/ Shower) | Bathtub | Bidet | Combination Sink And Tray | Combination Sink W/Food Disposal | Dental Unit or Cuspidor | Dental Lavatory | Drinking Fountain | Dishwasher Domestic | Floor Drain | Kitchen Sink Domestic | Kitchen Sink W/ Food Disposal | Lavatory (Small P.O.) | Lavatory (Large P.O.) | Lavatory, Barber, Beauty Parlor | Lavatory, Surgeon'S | Laundry Tray (1 or 2 Comparts.) | Shower Stall, Domestic | Showers ( Group) Per Head | Surgeons Sink | Flushing Rim Sink (W/ Valve) | Service Sink (Trap Standard) | Service Sink ( P Trap) | Pot Sink, Scullery Sink…Etc | Urinal, Pedestal, Siphon Jet, Blowout | Urinal, Wall Lip | Urinal Stall, Washout | Urinal Trough (Each 2 Feet Section) | Wash Sink, Each Set of Faucets | Water Closet (Tank Operated) | Water Closet (Valve Operated) | Fixture Drain or Trap Size 1 1/4 Inch | Fixture Drain or Trap Size 1 1/2 Inch | Fixture Drain or Trap Size 2 Inch | Fixture Drain or Trap Size 2 1/2 Inch | Fixture Drain or Trap Size 3 Inch | Fixture Drain or Trap Size 4 Inch | [8 empty] | 6 | 620 | 0 |  |  |  | 15 | 30 | 125 | 300 | 1100
[6 empty] | 6 | 8 | 2 | 3 | 3 | 3 | 4 | 1 | 1 | 0.5 | 2 | 1 | 2 | 3 | 1 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 8 | 3 | 2 | 4 | 8 | 4 | 4 | 2 | 2 | 4 | 8 | 1 | 2 | 3 | 4 | 5 | 6 | [8 empty] | 6 | 960 | 0 |  |  |  |  | 24 | 100 | 250 | 1000
[53 empty] | 6 | 1900 | 0 |  |  |  |  | 20 | 70 | 200 | 700
0
[53 empty] | 8 | 600 | 0 | [5 empty] | 50 | 150 | 500 | 1300
[53 empty] | 8 | 1400 | 0 | [5 empty] | 40 | 100 | 400 | 1200
[53 empty] | 8 | 2200 | 0 | [5 empty] | 30 | 80 | 350 | 1100
[53 empty] | 8 | 3600 | 0 | [5 empty] | 25 | 60 | 250 | 800
0
[53 empty] | 10 | 1000 | 0 | [6 empty] | 75 | 125 | 1000
[53 empty] | 10 | 2500 | 0 | [6 empty] | 50 | 100 | 500
[53 empty] | 10 | 3800 | 0 | [6 empty] | 30 | 80 | 350
[53 empty] | 10 | 5600 | 0 | [6 empty] | 25 | 60 | 250
[53 empty] | units | 0
[53 empty] | category | factor | INVERSE factor | linkcell | CHANGE CELL
[53 empty] | Length | 3.28 | 1 | 2 | 2
Note on D6: From the most remote vented fixture to the roof vent cap.
Reset Sanitary Fixtures Table
Network Data
Print
Options
Back
Normal View
Add/Copy/Modify/Delete Pipe
Units
S.I
British

## PIPULATOR (hidden)
|  | Pipulator |  | Pipulator | [21 empty] | STEEL SHCEDULE 40 | 6 | [11 empty] | STANDARD |  |  |  | EQUAL FRICTION |  |  | EQUAL VELOCITY |  |  | WATER DYNAMIC DATA
1 | OUT OF RANGE | [24 empty] | STEEL SHCEDULE 80 | [9 empty] | S.I. | 1
1 | [8 empty] | Pipe Material | [16 empty] | COPPER TYPE M | [9 empty] | BRITISH |  |  |  | SI |  | BRITISH | SI |  | BRITISH | SI |  | BRITISH | SI |  | BRITISH
1 | [25 empty] | COPPER TYPE L
1 | [25 empty] | COPPER TYPE K | [13 empty] | MIN DIAM (INCH) |  | MIN DIAM (INCH) | MIN DIAM (INCH) |  | MIN DIAM (INCH) | MIN DIAM (INCH) |  | MIN DIAM (INCH)
[26 empty] | Polypropylene PN20 | [13 empty] | 0 |  | 0 | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE!
136
[41 empty] | MIN DIAM (INCH) |  |  | MIN DIAM (INCH) |  |  | MIN DIAM (INCH)
[41 empty] | 0 |  |  | #VALUE! |  |  | #VALUE!
| Ser. No. | Pipe Code | Flow Rate |  | Velocity |  | Friction Losses |  | Outside Dia.
| 1 | Pipe Code |  | Lps |  | m/s |  | Pa/m |  | mm | [30 empty] | STAND. INT DIAM (INCH) |  |  | STAND. INT DIAM (INCH) |  |  | STAND. INT DIAM (INCH) |  |  | STAND. INT DIAM (INCH)
[41 empty] | 0 |  |  | #VALUE! |  |  | #VALUE! |  |  | 0
[11 empty] | WATER DYNAMIC DATA | EQUAL VELOCITY METHOD | [5 empty] | EQUAL FRICTION METHOD | [5 empty] | STANDARD METHOD | [5 empty] | Polypropylene PN20 | COPPER TYPE K | COPPER TYPE L | COPPER TYPE M | STEEL SCH. 80 | STEEL
[30 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 10
[11 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0.653 | 0.527 | 0.545 | 0.569 | 0.546 | 0.622 | 25 |  |  |  | VELOCITY (M/S) |  | VELOCITY (FT/S) | VELOCITY (M/S) |  | VELOCITY (FT/S) |  |  |  | VELOCITY (M/S) |  | VELOCITY (FT/S)
[11 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0.835 | 0.745 | 0.785 | 0.811 | 0.742 | 0.824 | 32 |  |  |  | N/A |  | #VALUE! | #VALUE! |  | #VALUE! |  |  |  | N/A |  | #VALUE!
[11 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 1.047 | 0.995 | 1.025 | 1.055 | 0.957 | 1.049 | 40
[11 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 1.315 | 1.245 | 1.265 | 1.291 | 1.278 | 1.38 | 50 |  |  |  |  | VELOCITY |  |  | VELOCITY | [5 empty] | VELOCITY
[11 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 1.653 | 1.481 | 1.505 | 1.527 | 1.5 | 1.61 | 63 |  |  |  |  | N/A |  |  | #VALUE! | [5 empty] | N/A
[11 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 1.969 | 1.959 | 1.985 | 2.009 | 1.939 | 2.067 | 75
[11 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 2.362 | 2.435 | 2.465 | 2.495 | 2.323 | 2.469 | 90
[11 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 2.89 | 2.907 | 2.945 | 2.981 | 2.9 | 3.068 | 110 |  |  |  | FRICTION LOSSES (PA/M) |  | FRICTION LOSSES (PSI/100FT) |  |  |  | FRICTION LOSSES (PA/M) |  | FRICTION LOSSES (PSI/100FT) | FRICTION LOSSES (PA/M) |  | FRICTION LOSSES (PSI/100FT)
[11 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 3.285 | 3.385 | 3.425 | 3.459 | 3.364 | 3.548 | 125 |  |  |  | N/A |  | #VALUE! |  |  |  | #VALUE! |  | #VALUE! | N/A |  | #VALUE!
[11 empty] | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 4.205 | 3.857 | 3.905 | 3.935 | 3.826 | 4.026 | 160
[11 empty] | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.805 | 4.875 | 4.907 | 4.813 | 5.047
[11 empty] | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 |  | 5.741 | 5.845 | 5.881 | 5.761 | 6.065
[11 empty] | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 7.785 | 7.625 | 7.981 | [5 empty] | FRICTION LOSSES | [5 empty] | FRICTION LOSSES |  |  | FRICTION LOSSES
[11 empty] | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 9.564 | 10.02 | [5 empty] | N/A | [5 empty] | #VALUE! |  |  | N/A
[11 empty] | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 11.376 | 12.09
[11 empty] | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 12.5 | 13.125
[11 empty] | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 14.314 | 15
[11 empty] | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 16.126 | 16.874
[11 empty] | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 17.938 | 18.814
[11 empty] | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 21.564 | 22.626
[30 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | STAND. INT DIAM (INCH) FOR STAND. METHOD
[30 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | STAND. DIAM (INCH)
[30 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | STAND. INT DIAM (INCH) FOR EQUAL FRICTION METHOD
[30 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | STAND. DIAM (INCH)
[30 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | STAND. INT DIAM (INCH) FOR EQUAL VELOCITY METHOD
[30 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | STAND. DIAM (INCH)
[30 empty] | 0 | 10.546 | 10.72 | 18.573 | 121.581 | 127.642 |  | 0 | STAND. INT DIAM (INCH) FOR WATER DYNAMIC DATA
[30 empty] | 1 | 0 | 0 | 0 | 0 | 0
Actual Friction Losses
0
Actual Velocity
0
Standard Method
Equal Friction Method
Equal Velocity Method
Dynamic Water Data
Back
Calculation Method
Units

## Dialog_add_delete_CW_HW_PIPE_ (hidden)
Add/Copy/Modify/Delete Pipe
Add New Pipe
Cancel
Copy Pipe
Add Pipe Feeding Two Existing Pipes
Modify Pipe Feeding Two Existing Pipes
Delete Pipe

## COLD & HOT WATER PIPES_ (hidden)
| CW & HW Pipe | [39 empty] | STEEL | 3 | mm |  | Steel Sch. 40 | Copper (types K, L, M) | Polypropylene PN20
1 | [34 empty] | Pipe Material |  |  |  | TD-F TANK |  | COPPER |  |  | Pipe Size mm (inch) | Flow (Lps) | Flow (Lps) | Flow (Lps)
[39 empty] | TD-F VALVE |  | POLYPROPYLENE PN20 |  |  | 0 | 0 | 0 | 0
[39 empty] | CW-F TANK |  |  |  |  | 25 | 0.24 | 0.26 | 0.26
[39 empty] | CW-F VALVE |  |  |  |  | 32 | 0.4 | 0.37 | 0.44
[39 empty] | HW |  |  |  |  | 40 | 0.65 | 0.6 | 0.67
[44 empty] | 50 | 1.15 | 0.87 | 1.06
| Ser. No. | Pipe Code | Separate Demand |  | Quantity of Fixtures on The Pipe | [24 empty] | Total Fixture Units |  | Type of Demand & Flushing | Demand Corresponds to Total Fixture Units |  | Pipe Demand |  | Outside Dia. |  |  | IF THERE IS FLUSH VALVE =1 IF NOT =0 | MSGBOX IF_THERE_IS_FLUSH_VALVE | DEMAND CORRESPONDS TO TOTAL FIXTURE UNITS (LPS) | PIPE SIZE | 63 | 1.5 | 1.6 | 1.68
[5 empty] | Pub. WC (F Valve) | Pub. WC (F Tank) | Pub. Pedestal UR (F Valve) | Pub. Wall UR (F Valve) | Pub. Wall UR (F Tank) | Pub. Lavatory (Faucet) | Pub. Bathtub (Faucet) | Pub. Shower (Mix. Valve) | Office Serv. Sink (Faucet) | Hotel Kitchen Sink (Faucet) | Priv. WC (F Valve) | Priv. WC (F Tank) | Priv. Lavatory (Faucet) | Priv. Bathtub (Faucet) | Priv. Shower (Mix. Valve) | Priv. Group (F Valve) | Priv. Group (F Tank) | Priv. Separate Shower (Mix. Valve) | Priv. Kitchen Sink (Faucet) | Priv. Laundry Trays (1-3 Faucet) | Priv. Combination Fixt. (Faucet) | Miscellaneous | Miscellaneous | Miscellaneous | Miscellaneous | [14 empty] | 75 | 2.5 | 2.5 | 2.39
[5 empty] | 10 | 5 | 10 | 5 | 3 | 2 | 4 | 4 | 3 | 4 | 6 | 3 | 1 | 2 | 2 | 8 | 6 | 2 | 2 | 3 | 3 | 0.25 | 0.5 | 1 | 2 | [14 empty] | 90 | 4.8 | 5 | 4.15
| 1 |  |  | Lps | [25 empty] | 0 | FU | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | 0 | #VALUE! | #VALUE! | #VALUE! | 110 | 8 | 8 | 7.07
[44 empty] | 160 | 18 | 18 | 18.9
|  |  | TD |  | 10 | 5 | 10 | 5 | 3 | 2 | 4 | 4 | 3 | 4 | 6 | 3 | 1 | 2 | 2 | 8 | 6 | 2 | 2 | 3 | 3 | 0.25 | 0.5 | 1 | 2 | [15 empty] | 30 | 31
|  |  | CW |  | 10 | 5 | 10 | 5 | 3 | 1.5 | 3 | 3 | 2.25 | 3 | 6 | 3 | 0.75 | 1.5 | 1.5 | 6 | 4.5 | 1.5 | 1.5 | 2.25 | 2.25 | 0.25 | 0.5 | 1 | 2 | [15 empty] | 50 | 50
|  |  | HW |  | 0 | 0 | 0 | 0 | 0 | 1.5 | 3 | 3 | 2.25 | 3 | 0 | 0 | 0.75 | 1.5 | 1.5 | 2.25 | 2.25 | 1.5 | 1.5 | 2.25 | 2.25 | 0.25 | 0.5 | 1 | 2 | [15 empty] | 100 | 0
[45 empty] | 150 | 0 | 0
[45 empty] | 220 | 0 | 0
[45 empty] | 260 | 0 | 0
[45 empty] | 330 | 0 | 0
[45 empty] | 430 | 0 | 0
| MAI PLUMBING CALCULATIONS | [23 empty] | Domestic Clod & Hot Water Pipes | [19 empty] | 520 | 0 | 0
[45 empty] | 800 | 0 | 0
| Project: | [23 empty] | Building:
| Client: | [23 empty] | Floor:
| Contractor: | [23 empty] | Network Code:
| Engineer: | [23 empty] | Pipe Material: |  |  |  |  | Polypropylene Pn20
| Ser. No. | Pipe Code | Separate Demand |  | Quantity of Fixtures on The Pipe | [24 empty] | Total Fixtue Units |  | Type of Flushing | Demand Corresponds to Total Fixture Units |  | Total Demand |  | Outside Dia.
[5 empty] | Pub. WC (F Valve) | Pub. WC (F Tank) | Pub. Pedestal UR (F Valve) | Pub. Wall UR (F Valve) | Pub. Wall UR (F Tank) | Pub. Lavatory (Faucet) | Pub. Bathtub (Faucet) | Pub. Shower (Mix. Valve) | Office Serv. Sink (Faucet) | Hotel Kitchen Sink (Faucet) | Priv. WC (F Valve) | Priv. WC (F Tank) | Priv. Lavatory (Faucet) | Priv. Bathtub (Faucet) | Priv. Shower (Mix. Valve) | Priv. Group (F Valve) | Priv. Group (F Tank) | Priv. Separate Shower (Mix. Valve) | Priv. Kitchen Sink (Faucet) | Priv. Laundry Trays (1-3 Faucet) | Priv. Combination Fixt. (Faucet) | Miscellaneous | Miscellaneous | Miscellaneous | Miscellaneous
[5 empty] | FU 10T/10C | FU 5T/5C | FU 10T/10C | FU 5T/5C | FU 3T/3C | FU 2T/1.5C/1.5H | FU 4T/3C/3H | FU 4T/3C/3H | FU 3T/2.25C/2.25H | FU 4T/3C/3H | FU 6T/6C | FU 3T/3C | FU 1T/0.75C/0.75H | FU 2T/1.5C/1.5H | FU 2T/1.5C/1.5H | FU 8T/6C/2.25H | FU 6T/4.5C/2.25H | FU 2T/1.5C/1.5H | FU 2T/1.5C/1.5H | FU 3T/2.25C/2.25H | FU 3T/2.25C/2.25H | 0.25FU | 0.5 FU | 1 FU | 2 FU
[44 empty] | units | 0
[44 empty] | category | factor | INVERSE factor | linkcell | CHANGE CELL
[44 empty] | Discharge | 1 | 15.85 | 1 | 1
Total Demand
Separate Cold water Demand
Separate Hot Water Demand
Network Data
Print
Options
Back
Demand Type
Normal View
Reset Sanitary Fixtures Table
Add/Copy/Modify/Delete Pipe
Units
S.I
British

## HOT WATER RETURN PIPES (hidden)
| Hot Water Return Pipe Sizing | [6 empty] | STEEL | 3 | mm |  | Steel Sch. 40 | Copper (types K, L, M) | Polypropylene PN20
[8 empty] | COPPER |  |  | Pipe Size mm (inch) | Flow (Lps) | Flow (Lps) | Flow (Lps)
Temperature Diffirence (oC) | [5 empty] | Pipe Material |  | Polypropylene PN20 |  |  | 0 | 0 | 0 | 0
10 | [10 empty] | 25 | 0.24 | 0.26 | 0.26
[11 empty] | 32 | 0.4 | 0.37 | 0.44
Ser. No. | Pipe Code | Pipe Length |  | Disharge |  | Outside Dia. |  | PIPE SIZE |  |  | 40 | 0.65 | 0.6 | 0.67
1 | Pipe Code | 0 | m | 0 | Lps | #VALUE! | #VALUE! | #VALUE! |  |  | 50 | 1.15 | 0.87 | 1.06
[11 empty] | 63 | 1.5 | 1.6 | 1.68
[11 empty] | 75 | 2.5 | 2.5 | 2.39
[11 empty] | 90 | 4.8 | 5 | 4.15
[11 empty] | 110 | 8 | 8 | 7.07
[11 empty] | 160 | 18 | 18 | 18.9
[12 empty] | 30 | 31
[12 empty] | 50 | 50
[12 empty] | 100 | 0
[12 empty] | 150 | 0 | 0
[12 empty] | 220 | 0 | 0
[12 empty] | 260 | 0 | 0
[12 empty] | 330 | 0 | 0
[12 empty] | 430 | 0 | 0
MAI PLUMBING CALCULATIONS |  |  |  |  | Hot Water Return Pipes | [6 empty] | 520 | 0 | 0
[12 empty] | 800 | 0 | 0
Project: |  |  |  |  | Building:
Client: |  |  |  |  | Floor:
Contractor: |  |  |  |  | Network Code:
Engineer: |  |  |  |  | Temp. Diff. (oC): | 10
[5 empty] | Pipe Material: | Polypropylene Pn20
Ser. No. | Pipe Code | Pipe Length |  | Disharge |  | Outside Dia.
#REF!
#REF!
[8 empty] | #REF! |  |  | units | 0
[8 empty] | #REF! |  |  | category | factor | INVERSE factor | linkcell | CHANGE CELL
[8 empty] | #REF! |  |  | length | 1 | 3.28 | 1 | 1
[8 empty] | #REF! |  |  | Discharge | 1 | 15.85
[8 empty] | #REF! |  |  | Temp diff | 1 | 1.8
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
Note on B3: 20 OF (11.1 oC) is recommended by ASHRAE
Network Data
Add/Modify/Delete Pipe
Print
Options
Back
Units
S.I
British

## COMPRESSED AIR PIPES (hidden)
|  | Compressed Air Pipe Sizing | [6 empty] | 60 PSIG | 1 |  | ALLOWABLE FLOW RATES FOR COMPRESSED AIR PIPING STANDARD WEIGHT STEEL PIPE AND 60 PSI COMPRESSED AIR (FROM CAPITOLINE) | ALLOWABLE FLOW RATES FOR COMPRESSED AIR PIPING STANDARD WEIGHT STEEL PIPE AND 100 PSI COMPRESSED AIR (FROM CAPITOLINE)
*N.B.1 This sizing is based on standard weight steel pipes. | [8 empty] | 100 PSIG |  | PIPE SIZE (INCH) | FLOW RATE (FREE AIR) (SCFM) | FLOW RATE (FREE AIR) (SCFM)
*N.B.2 This pipe sizing has been done according to CAPITOLINE standard. | [11 empty] | 0 | 0
*N.B.3 Standard Cubic Feet per Minute (SCFM) is the design capacity under the free air (with normal atmospheric conditions (70oF & 1 Bar)): | [10 empty] | 0.5 | 12 | 15
[7 empty] | Working Pressure |  |  |  | 0.75 | 25 | 32
[11 empty] | 1 | 48 | 60
| Ser. No. | Pipe Code | Total Discharge |  | Pipe Size |  |  |  | PIPE SIZE |  | 1.25 | 100 | 125
| 1 | Pipe Code |  | SCFM | #VALUE! | #VALUE! |  |  | #VALUE! |  | 1.5 | 155 | 197
[11 empty] | 2 | 290 | 360
[11 empty] | 2.5 | 475 | 580
[11 empty] | 3 | 825 | 1100
[11 empty] | 4 | 1750 | 2150
[11 empty] | 5 | 3100 | 3900
[11 empty] | 6 | 5100 | 6300
[11 empty] | 8 | 10900 | 13100
[11 empty] | 10 | 19500 | 24000
[11 empty] | 12 | 30500 | 35000
| MAI PLUMBING CALCULATIONS |  |  |  |  | Compressed Air Pipes
| Project: |  |  |  |  | Building:
| Client: |  |  |  |  | Floor:
| Contractor: |  |  |  |  | Network Code:
| Engineer: |  |  |  |  | Working Pressure: |  | 60 PSIG
| Ser. No. | PIPE CODE | Total Discharge |  | Pipe Size
#REF!
#REF!
#REF!
#REF!
Note on F7: Sizing is based on 1 Psi/100ft max. pressure drop.
Network Data
Add/Modify/Delete Pipe
Print
Options
Back

## VACUUM AIR PIPES (hidden)
Vacuum Air Pipe Sizing
*N.B. This pipe sizing has been done according to CAPITOLINE standard.
ALLOWABLE FLOW RATES FOR VACUUM PIPING (IN CAPITOLINE)
| Ser. No. | Pipe Code | Total Discharge |  | Pipe Size |  |  | PIPE SIZE |  | 0
| 1 | Pipe Code |  | CFM | #VALUE! | #VALUE! |  | #VALUE! | 0.5 | 4
[9 empty] | 0.75 | 9
[9 empty] | 1 | 20
[9 empty] | 1.25 | 35
[9 empty] | 1.5 | 60
[9 empty] | 2 | 110
[9 empty] | 2.5 | 170
[9 empty] | 3 | 250
[9 empty] | 4 | 435
| MAI PLUMBING CALCULATIONS | [5 empty] | Vacuum Air Pipes
| Project: | [5 empty] | Building:
| Client: | [5 empty] | Floor:
| Contractor: | [5 empty] | Network Code:
Engineer:
| Ser. No. | Pipe Code | Total Discharge |  | Pipe Size
#REF!
#REF!
#REF!
#REF!
Note on F5: Sizing is based on 1 inch Hg/100ft max. pressure drop & 5000 Fpm max. velocity
Network Data
Add/Modify/Delete Pipe
Print
Options
Back

## GAS PIPES (hidden)
| Gas Pipe Sizing | [31 empty] | GENERAL FOR ALL PIPES | [12 empty] | FOR THE MAIN PIPE
2 | [8 empty] | Units Conversion Table | [19 empty] | Used Gas
[9 empty] | From |  |  |  | To
[9 empty] | 1 |  | Kg/Hr |  | 46.6972 |  | Cfh
[9 empty] | 1 |  | KW |  | 2.5097 |  | Cfh
[9 empty] | 1 |  | Btu/Hr |  | 0.00073534 |  | Cfh
[9 empty] | 1 |  | inch W.C |  | 0.03613 |  | Psi | [17 empty] | TEMP. (OF) | ABSOLUTE TEMP. (OF) (t(OF)+460) | [9 empty] | STEEL | COPPER
Total Length of The Main Pipe | [32 empty] | 60 | 520 | [9 empty] | 0 | 0 |  |  |  |  | SCREWED FITTINGS |  |  |  | 90O WELDING ELBOWS AND SMOOTH BENDS | [5 empty] | MITER ELBOWS (NO. OF MITERS) |  |  |  |  | WELDING TEES |  | VALVES (SCREWED, FLANGED OR WELDED) |  |  |  | TOTAL EQUIVELENT LENGTH FOR ALL FITTINGS
Maximum Working Pressure on The Main Pipe | Maximum Working Pressure On The Main Pipe | Pressure Drop Through The Whole Length of The Main Pipe | Pressure Drop Through The Whole Length Of The Main Pipe | Total Flow Rate in The Main Pipe | Total Flow Rate In The Main Pipe | Length of The Main Pipe between The Supply Regulator And The Furthest Regulator | Measured Length Of The Main Pipe | Quantity of Fittings on The Main Pipe | [20 empty] | Equiv. Length for Fittings And Valves on The Main Pipe | Equiv. Length For Fittings And Valves On The Main Pipe | Total Length of The Main Pipe | Total Length Of The Main Pipe | [10 empty] | 0.25 | 0.364 | 0.311 |  |  |  |  | 45O ell | 90O ell | 180O close return bend | Tee | R/D=1 | R/D=1 1/3 | R/D=2 | R/D=4 | R/D=6 | R/D=8 | 1-45O | 1-60O | 1-90O | 2-90O | 3-90O | Forged | Miter | Gate | Globe | Angle | Swing Chech
Maximum Working Pressure On The Main Pipe | Maximum Working Pressure On The Main Pipe | Pressure Drop Through The Whole Length Of The Main Pipe | Pressure Drop Through The Whole Length Of The Main Pipe | Total Flow Rate In The Main Pipe | Total Flow Rate In The Main Pipe | Measured Length Of The Main Pipe | Measured Length Of The Main Pipe | Screwed Fittings | Screwed Fittings | Screwed Fittings | Screwed Fittings | 90O Welding Elbows And Smooth Bends | 90O Welding Elbows And Smooth Bends | 90O Welding Elbows And Smooth Bends | 90O Welding Elbows And Smooth Bends | 90O Welding Elbows And Smooth Bends | 90O Welding Elbows And Smooth Bends | Miter Elbows (No. of Miters) | Miter Elbows (No. Of Miters) | Miter Elbows (No. Of Miters) | Miter Elbows (No. Of Miters) | Miter Elbows (No. Of Miters) | Welding Tees | Welding Tees | Valves (Screwed, Flanged or Welded) | Valves (Screwed, Flanged Or Welded) | Valves (Screwed, Flanged Or Welded) | Valves (Screwed, Flanged Or Welded) | Equiv. Length For Fittings And Valves On The Main Pipe | Equiv. Length For Fittings And Valves On The Main Pipe | Total Length Of The Main Pipe | Total Length Of The Main Pipe | FUEL_PIPES_add_equiv_length | #VALUE! | [8 empty] | 0.375 | 0.493 | 0.402 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum Working Pressure On The Main Pipe | Maximum Working Pressure On The Main Pipe | Pressure Drop Through The Whole Length Of The Main Pipe | Pressure Drop Through The Whole Length Of The Main Pipe | Total Flow Rate In The Main Pipe | Total Flow Rate In The Main Pipe | Measured Length Of The Main Pipe | Measured Length Of The Main Pipe | 45O Elbow | 90O Elbow | 180O Close Return Bend | Tee | R/D=1 | R/D=1 1/3 | R/D=2 | R/D=4 | R/D=6 | R/D=8 | 1-45O | 1-60O | 1-90O | 2-90O | 3-90O | Forged | Miter | Gate | Globe | Angle | Swing Check | Equiv. Length For Fittings And Valves On The Main Pipe | Equiv. Length For Fittings And Valves On The Main Pipe | Total Length Of The Main Pipe | Total Length Of The Main Pipe | fittings_quantity | 0 |  |  | DENSITY (KG/M3)(IN 60O F TEMP) | SPECEFIC GRAVITY | VISCOSITY (CENTIPOISE)(IN 60O F TEMP) | SUPEREXPANSIBILITY FACTOR | Heating value (MJ/Kg) |  | 0.5 | 0.622 | 0.527 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Psi |  | Psi |  | Cfh |  | Ft | [22 empty] | Ft | 0 | Ft |  |  | 2 | METHANE (CH4) | 0.679 | 0.53913 | 0.0111 | 0.84032 | 52.665 | 0 | 0.75 | 0.824 | 0.745
[33 empty] | MaxPress,PressDrop | #VALUE! |  | NATURAL GAS | 0.75567 | 0.6 | 0.012 | 1 | 38.25 | 1 | 1 | 1.049 | 0.995
[36 empty] | PROPANE (C3H8) | 1.92 | 1.5245 | 0.008 | 0.992 | 48.3875 | 0 | 1.25 | 1.38 | 1.245
[36 empty] | BUTANE (C4H10) | 2.53 | 2.0088 | 0.0076 | 7.8503 | 47.682 | 0 | 1.5 | 1.61 | 1.481
Ser. No. | Ser. No. | Pipe Code | Pipe Code | Flow Rate | Flow Rate | Flow Rate | Flow Rate | Pipe Size | Pipe Size | Pipe Size | Pipe Size | [21 empty] | PIPE SIZE | FUEL_PIPES_BIGGER_THAN_TOTAL_DISCHARGE |  | PROPYLENE (C3H6) | 1.78 | 1.4133 | 0.0087 | 4.2352 | 47.375 | 0 | 2 | 2.067 | 1.959
1 |  | Pipe Code | Pipe Code |  |  | Cfh |  | 0 |  | Inch | [22 empty] | 0 | #VALUE! |  | ACETYLENE (C2H2) | 1.12 | 0.88928 | 0.0101 | 1.9634 | 49.1685 | 0 | 2.5 | 2.469 | 2.435
[36 empty] | HYDROGEN SULFIDE (H2S) | 1.456 | 1.1561 | 0.0125 | 3.3136 | 15.8565 | 0 | 3 | 3.068 | 2.907
[37 empty] | 0.75567 | 0.6 | 0.012 | 1 | 38.25 |  | 4 | 4.026 | 3.857 | [6 empty] | MAIN PIPE SIZE
[43 empty] | 5 | 5.047 | 4.805 | [6 empty] | 0
MAI PLUMBING CALCULATIONS | [21 empty] | Gas Pipes | [15 empty] | MJ/m3 | 50.6175 |  |  |  | 6 | 6.065 | 5.741
[43 empty] | 8 | 7.981 | 0
Project: | [21 empty] | Building: | [20 empty] | 10 | 10.02 | 0
Client: | [21 empty] | Floor: | [20 empty] | 12 | 11.938 | 0
Contractor: | [21 empty] | Network Code:
Engineer: | [21 empty] | Used Fuel: |  |  | Natural Gas
[22 empty] | Pipe Material: |  |  |  | Copper Tubes
Total Length Of The Main Pipe
Maximum Working Pressure On The Main Pipe | Maximum Working Pressure On The Main Pipe | Pressure Drop Through The Whole Length of The Main Pipe | Pressure Drop Through The Whole Length Of The Main Pipe | #VALUE! | Total Flow Rate In The Main Pipe | Measured Length of The Main Pipe | Measured Length Of The Main Pipe | Quantity of Fittings on The Main Pipe | [20 empty] | Equiv. Length for Fittings And Valves on The Main Pipe | Equiv. Length For Fittings And Valves On The Main Pipe | Total Length Of The Main Pipe | Total Length Of The Main Pipe | [15 empty] | Table C-2 IN NFPA-54 (EQUIVALENT LENGTH FOR DIFFERENT FITTINGS AND VALVES)
Maximum Working Pressure On The Main Pipe | Maximum Working Pressure On The Main Pipe | Pressure Drop Through The Whole Length Of The Main Pipe | Pressure Drop Through The Whole Length Of The Main Pipe | Total Flow Rate In The Main Pipe | Total Flow Rate In The Main Pipe | Measured Length Of The Main Pipe | Measured Length Of The Main Pipe | Screwed Fittings | Screwed Fittings | Screwed Fittings | Screwed Fittings | 90O Welding Elbows And Smooth Bends | 90O Welding Elbows And Smooth Bends | 90O Welding Elbows And Smooth Bends | 90O Welding Elbows And Smooth Bends | 90O Welding Elbows And Smooth Bends | 90O Welding Elbows And Smooth Bends | Miter Elbows (No. of Miters) | Miter Elbows (No. Of Miters) | Miter Elbows (No. Of Miters) | Miter Elbows (No. Of Miters) | Miter Elbows (No. Of Miters) | Welding Tees | Welding Tees | Valves (Screwed, Flanged or Welded) | Valves (Screwed, Flanged Or Welded) | Valves (Screwed, Flanged Or Welded) | Valves (Screwed, Flanged Or Welded) | Equiv. Length For Fittings And Valves On The Main Pipe | Equiv. Length For Fittings And Valves On The Main Pipe | Total Length Of The Main Pipe | Total Length Of The Main Pipe | [17 empty] | Screwed fittings2 |  |  |  | 90º welding elbows and smooth bends3 | [5 empty] | Miter elbows4 (No. of miters) |  |  |  |  | Welding tees |  | Valves (screwed, flanged, or welded)
Maximum Working Pressure On The Main Pipe | Maximum Working Pressure On The Main Pipe | Pressure Drop Through The Whole Length Of The Main Pipe | Pressure Drop Through The Whole Length Of The Main Pipe | Total Flow Rate In The Main Pipe | Total Flow Rate In The Main Pipe | Measured Length Of The Main Pipe | Measured Length Of The Main Pipe | 45O Elbow | 90O Elbow | 180O Close Return Bend | Tee | R/D=1 | R/D=1 1/3 | R/D=2 | R/D=4 | R/D=6 | R/D=8 | 1-45O | 1-60O | 1-90O | 2-90O | 3-90O | Forged | Miter | Gate | Globe | Angle | Swing Check | Equiv. Length For Fittings And Valves On The Main Pipe | Equiv. Length For Fittings And Valves On The Main Pipe | Total Length Of The Main Pipe | Total Length Of The Main Pipe | [19 empty] | 180º close | [7 empty] | 1-45º | 1-60º | 1-90º | 2-90º | 3-90º | Forged | Miter4 | Gate | Globe | Angle | check
[50 empty] | 45ºell | 90ºell | return bends | Tee | R/d = 1 | R/d = 11/3 | R/d = 2 | R/d = 4 | R/d = 6 | R/d = 8 | 0.45 | 0.9 | 1.8 | 0.6 | 0.45 | 1.35 | 1.8 | 0.21 | 10 | 5 | 2.5
[48 empty] | k factor = |  | 0.42 | 0.9 | 2 | 1.8 | 0.48 | 0.36 | 0.27 | 0.21 | 0.27 | 0.36 | 15 | 30 | 60 | 20 | 15 | 45 | 60 | 7 | 333 | 167 | 83
[48 empty] | L/d¢ ratio5 n = |  | 14 | 30 | 67 | 60 | 16 | 12 | 9 | 7 | 9 | 12
Ser. No. | Ser. No. | Pipe Code | Pipe Code | Flow Rate | Flow Rate | Flow Rate | Flow Rate | Pipe Size | Pipe Size | Pipe Size | Pipe Size
[48 empty] | Nominal pipe size (inch) | Inside diam. d (inch, sch. 40) | L = equivalent length in feet of Schedule 40 (standard weight) straight pipe7
[47 empty] | 0 | 0.5 | 0.622 | 0.73 | 1.55 | 3.47 | 3.1 | 0.83 | 0.62 | 0.47 | 0.36 | 0.47 | 0.62 | 0.78 | 1.55 | 3.1 | 1.04 | 0.78 | 2.33 | 3.1 | 0.36 | 17.3 | 8.65 | 4.32
[47 empty] | 0 | 0.75 | 0.824 | 0.96 | 2.06 | 4.6 | 4.12 | 1.1 | 0.82 | 0.62 | 0.48 | 0.62 | 0.82 | 1.03 | 2.06 | 4.12 | 1.37 | 1.03 | 3.09 | 4.12 | 0.48 | 22.9 | 11.4 | 5.72
[47 empty] | 0 | 1 | 1.049 | 1.22 | 2.62 | 5.82 | 5.24 | 1.4 | 1.05 | 0.79 | 0.61 | 0.79 | 1.05 | 1.31 | 2.62 | 5.24 | 1.75 | 1.31 | 3.93 | 5.24 | 0.61 | 29.1 | 14.6 | 7.27
[47 empty] | 0 | 1.25 | 1.38 | 1.61 | 3.45 | 7.66 | 6.9 | 1.84 | 1.38 | 1.03 | 0.81 | 1.03 | 1.38 | 1.72 | 3.45 | 6.9 | 2.3 | 1.72 | 5.17 | 6.9 | 0.81 | 38.3 | 19.1 | 9.58
[47 empty] | 0 | 1.5 | 1.61 | 1.88 | 4.02 | 8.95 | 8.04 | 2.14 | 1.61 | 1.21 | 0.94 | 1.21 | 1.61 | 2.01 | 4.02 | 8.04 | 2.68 | 2.01 | 6.04 | 8.04 | 0.94 | 44.7 | 22.4 | 11.2
1
[47 empty] | 0 | 2 | 2.067 | 2.41 | 5.17 | 11.5 | 10.3 | 2.76 | 2.07 | 1.55 | 1.21 | 1.55 | 2.07 | 2.58 | 5.17 | 10.3 | 3.45 | 2.58 | 7.75 | 10.3 | 1.21 | 57.4 | 28.7 | 14.4
[47 empty] | 0 | 2.5 | 2.469 | 2.88 | 6.16 | 13.7 | 12.3 | 3.29 | 2.47 | 1.85 | 1.44 | 1.85 | 2.47 | 3.08 | 6.16 | 12.3 | 4.11 | 3.08 | 9.25 | 12.3 | 1.44 | 68.5 | 34.3 | 17.1
[47 empty] | 0 | 3 | 3.068 | 3.58 | 7.67 | 17.1 | 15.3 | 4.09 | 3.07 | 2.3 | 1.79 | 2.3 | 3.07 | 3.84 | 7.67 | 15.3 | 5.11 | 3.84 | 11.5 | 15.3 | 1.79 | 85.2 | 42.6 | 21.3
[47 empty] | 0 | 4 | 4.026 | 4.7 | 10.1 | 22.4 | 20.2 | 5.37 | 4.03 | 3.02 | 2.35 | 3.02 | 4.03 | 5.04 | 10.1 | 20.2 | 6.71 | 5.04 | 15.1 | 20.2 | 2.35 | 112 | 56 | 28
[47 empty] | 0 | 5 | 5.047 | 5.88 | 12.6 | 28 | 25.2 | 6.72 | 5.05 | 3.78 | 2.94 | 3.78 | 5.05 | 6.3 | 12.6 | 25.2 | 8.4 | 6.3 | 18.9 | 25.2 | 2.94 | 140 | 70 | 35
1
[47 empty] | 0 | 6 | 6.065 | 7.07 | 15.2 | 33.8 | 30.4 | 8.09 | 6.07 | 4.55 | 3.54 | 4.55 | 6.07 | 7.58 | 15.2 | 30.4 | 10.1 | 7.58 | 22.8 | 30.4 | 3.54 | 168 | 84.1 | 42.1
[47 empty] | 0 | 8 | 7.981 | 9.31 | 20 | 44.6 | 40 | 10.6 | 7.98 | 5.98 | 4.65 | 5.98 | 7.98 | 9.97 | 20 | 40 | 13.3 | 9.97 | 29.9 | 40 | 4.65 | 222 | 111 | 55.5
[47 empty] | 0 | 10 | 10.02 | 11.7 | 25 | 55.7 | 50 | 13.3 | 10 | 7.51 | 5.85 | 7.51 | 10 | 12.5 | 25 | 50 | 16.7 | 12.5 | 37.6 | 50 | 5.85 | 278 | 139 | 69.5
[47 empty] | 0 | 12 | 11.94 | 13.9 | 29.8 | 66.3 | 59.6 | 15.9 | 11.9 | 8.95 | 6.96 | 8.95 | 11.9 | 14.9 | 29.8 | 59.6 | 19.9 | 14.9 | 44.8 | 59.6 | 6.96 | 332 | 166 | 83
[47 empty] | 0 | 14 | 13.13 | 15.3 | 32.8 | 73 | 65.6 | 17.5 | 13.1 | 9.85 | 7.65 | 9.85 | 13.1 | 16.4 | 32.8 | 65.6 | 21.9 | 16.4 | 49.2 | 65.6 | 7.65 | 364 | 182 | 91
1
[47 empty] | 0 | 16 | 15 | 17.5 | 37.5 | 83.5 | 75 | 20 | 15 | 11.2 | 8.75 | 11.2 | 15 | 18.8 | 37.5 | 75 | 25 | 18.8 | 56.2 | 75 | 8.75 | 417 | 208 | 104
[47 empty] | 0 | 18 | 16.88 | 19.7 | 42.1 | 93.8 | 84.2 | 22.5 | 16.9 | 12.7 | 9.85 | 12.7 | 16.9 | 21.1 | 42.1 | 84.2 | 28.1 | 21.1 | 63.2 | 84.2 | 9.85 | 469 | 234 | 117
[47 empty] | 0 | 20 | 18.81 | 22 | 47 | 105 | 94 | 25.1 | 18.8 | 14.1 | 11 | 14.1 | 18.8 | 23.5 | 47 | 94 | 31.4 | 23.5 | 70.6 | 94 | 11 | 522 | 261 | 131
[47 empty] | 0 | 24 | 22.63 | 26.4 | 56.6 | 126 | 113 | 30.2 | 22.6 | 17 | 13.2 | 17 | 22.6 | 28.3 | 56.6 | 113 | 37.8 | 28.3 | 85 | 113 | 13.2 | 629 | 314 | 157
[50 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on B9: 23 Psi for networks outside buildings & 5 Psi inside buildings.
Note on D9: Generally: 10 % of the max working pressure on the main pipe.
Iron Pipes (Steel Schedule 40) or Equivalent Rigid Pipe
Copper Tube (Type K) or Smooth Wall Semirigid Tubing
Add Equivalent Length for Fittings on The Main Pipe
Reset Total Pipe Length Table
Network Data
Add/Modify/Delete Pipe
Print
Options
Back
Pipe Material

## SUBMERSIBLE PUMP DISCHARGE (hidden)
Submersible Drainage Pump Discharge | [13 empty] | FLOW CORRESPONDS TO AREA PROJECTED TO RAIN WATER (LPS) | [9 empty] | PIPE SLOPE | DESIGN DEMAND CORRESPONDS TO DRAINAGE FIXTURE UNITS BASED ON TABLE 26.5 PAGE 26-17 IN NATIONAL PLUMBING CODE (LPS) |  |  | EQUATION FOR SLOPE 1% (1/8 IN./FT) |  | EQUATION FOR SLOPE 2% (1/4 IN./FT)
OUT OF RANGE | [13 empty] | RAIN FALL (Inch./Hr.) | FLOW (LPS) |  |  |  | STEEL | 1 |  |  |  | 1% | 0 | 1 |  | 4th Degree Polynomial Fit: y=a+bx+cx^2+dx^3... |  | 5th Degree Polynomial Fit: y=a+bx+cx^2+dx^3...
[14 empty] | 1 | 0 | 4 |  |  | COPPER |  |  |  |  | 2% | 0 |  |  | Coefficient Data: |  | Coefficient Data:
Gravity Drainage Pipe Slope | [10 empty] | Discharge Pipe Material |  |  | 2 |  |  |  |  | PLASTIC | [8 empty] | a = | 46.4556 | a = | 52.1016
[14 empty] | 3 | [13 empty] | b = | 0.22576 | b = | 0.2153
[14 empty] | 4 | [13 empty] | c = | -7.0902e-05 | c = | -5.4294e-05
[14 empty] | 5 | [13 empty] | d = | 2.1368e-08 | d = | 2.7512e-08
[14 empty] | 6 | [13 empty] | e = | -2.0648e-12 | e = | -6.0761e-12
[14 empty] | 7 | [15 empty] | f = | 4.7915e-16
[14 empty] | 8 | [7 empty] | Steel Sch. 40 |  |  | Copper (types K, L, M) |  |  | Plastic (Sch. 80)
[22 empty] | Pipe Size mm (inch) | Flow (Lps) |  | Pipe Size mm (inch) | Flow (Lps) |  | Pipe Size mm (inch) | Flow (Lps)
[21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | TOTAL DEMAND | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | 0 | [6 empty] | 0 | 0.5 | 0.24 | 0 | 0.5 | 0.26 | 0 | 0.5 | 0.18
[21 empty] | 0 | 0.75 | 0.4 | 0 | 0.75 | 0.37 | 0 | 0.75 | 0.3
[21 empty] | 0 | 1 | 0.65 | 0 | 1 | 0.6 | 0 | 1 | 0.5
[21 empty] | 0 | 1.25 | 1.15 | 0 | 1.25 | 0.87 | 0 | 1.25 | 1
[21 empty] | 0 | 1.5 | 1.5 | 0 | 1.5 | 1.6 | 0 | 1.5 | 1.3
[21 empty] | 0 | 2 | 2.5 | 0 | 2 | 2.5 | 0 | 2 | 2.2
[21 empty] | 0 | 2.5 | 4.8 | 0 | 2.5 | 5 | 0 | 2.5 | 4.4
MAI PLUMBING CALCULATIONS | [9 empty] | Submersible Drainage Pump Discharge | [10 empty] | 0 | 3 | 8 | 0 | 3 | 8 | 0 | 3 | 8
[21 empty] | 0 | 4 | 18 | 0 | 4 | 18 | 0 | 4 | 16
Project: | [9 empty] | Building: | [10 empty] | 0 | 5 | 30 | 0 | 5 | 31 | 0 | 5 | 26
Client: | [9 empty] | Floor: | [10 empty] | 0 | 6 | 50 | 0 | 6 | 50 | 0 | 6 | 50
Contractor: | [9 empty] | Axes: | [10 empty] | 0 | 8 | 100 | 0 | 0 | 0 | 0 | 8 | 90
Engineer: | [9 empty] | Pump No.: | 1 | [9 empty] | 0 | 10 | 150 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | Drainage Slope (%): |  | 1 | [8 empty] | 0 | 12 | 220 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | Pipe Material: |  | Steel | [8 empty] | 0 | 14 | 260 | 0 | 0 | 0 | 0 | 0 | 0
Separate Demand |  | Area Projected to Rain Water And Drained by The Pump |  | Rain Fall |  | Total Drainage Fixture Units |  | Demand Corresponds to Total Drainage Fixture Units |  | Pump Demand |  | Pipe Size | [8 empty] | 0 | 16 | 330 | 0 | 0 | 0 | 0 | 0 | 0
| Gpm |  | Ft2 | 4 | Inch/Hr | 0 | DFU | 0 | Gpm | 0 | Gpm | 0 | Inch | [7 empty] | 0 | 18 | 430 | 0 | 0 | 0 | 0 | 0 | 0
Drainage Fixture Units Per Fixture or Group | [20 empty] | 0 | 20 | 520 | 0 | 0 | 0 | 0 | 0 | 0
Fixture Type | [8 empty] | Fixture Unit Value As Load Factors |  | Minimum Size of Trap (In.) | Qty. | Total Fixture Units | units | [6 empty] | 0 | 24 | 800 | 0 | 0 | 0 | 0 | 0 | 0
1 Bathroom Group Consisting of Water Closet (Tank Opertated), Lavatory And Bathtub or Shower Stall | [8 empty] | 6 |  |  |  | 0 | category | factor | INVERSE factor | linkcell | CHANGE CELL |  |  |  | 0 |  |  | 0 |  |  | 0
1 Bathroom Group Consisting of Water Closet (Flush Valve Opertated), Lavatory And Bathtub or Shower Stall | [8 empty] | 8 |  |  |  | 0 | discharge | 15.85 | 1 | 2 | 2
Bathtub (With or Without Over Head Shower) | [8 empty] | 2 |  |  |  | 0 | Area | 10.7584 | 1
Bathtub | [8 empty] | 3 |  |  |  | 0 | [11 empty] | PIPE SIZE
Bidet | [8 empty] | 3 |  |  |  | 0 | [11 empty] | 0
Combination Sink And Tray | [8 empty] | 3 |  |  |  | 0
Combination Sink And Tray With Food Disposal Unit | [8 empty] | 4 |  |  |  | 0
Dental Unit or Cuspidor | [8 empty] | 1 |  |  |  | 0
Dental Lavatory | [8 empty] | 1 |  |  |  | 0
Drinking Fountain | [8 empty] | 0.5 |  |  |  | 0
Dishwasher Domestic | [8 empty] | 2 |  |  |  | 0
Floor Drain | [8 empty] | 1 |  |  |  | 0
Kitchen Sink Domestic | [8 empty] | 2 |  |  |  | 0
Kitchen Sink Domestic With Food Disposal Unit | [8 empty] | 3 |  |  |  | 0
Lavatory (Small P.O.) | [8 empty] | 1 |  |  |  | 0
Lavatory (Large P.O.) | [8 empty] | 2 |  |  |  | 0
Lavatory, Barber, Beauty Parlor | [8 empty] | 2 |  |  |  | 0
Lavatory, Surgeon'S | [8 empty] | 2 |  |  |  | 0
Laundry Tray (1 or 2 Compartments) | [8 empty] | 2 |  |  |  | 0
Shower Stall, Domestic | [8 empty] | 2 |  |  |  | 0
Showers ( Group) Per Head | [8 empty] | 3 |  |  |  | 0
Surgeons Sink | [8 empty] | 3 |  |  |  | 0
Flushing Rim Sink (With Valve) | [8 empty] | 8 |  |  |  | 0
Service Sink (Trap Standard) | [8 empty] | 3 |  |  |  | 0
Service Sink ( P Trap) | [8 empty] | 2 |  |  |  | 0
Pot Sink, Scullery Sink…Etc | [8 empty] | 4 |  |  |  | 0
Urinal, Pedestal, Siphon Jet, Blowout | [8 empty] | 8 |  |  |  | 0
Urinal, Wall Lip | [8 empty] | 4 |  |  |  | 0
Urinal Stall, Washout | [8 empty] | 4 |  |  |  | 0
Urinal Trough (Each 2 Feet Section) | [8 empty] | 2 |  |  |  | 0
Wash Sink (Circular or Multiple), Each Set of Faucets | [8 empty] | 2 |  |  |  | 0
Water Closet (Tank Operated) | [8 empty] | 4 |  |  |  | 0
Water Closet (Valve Operated) | [8 empty] | 8 |  |  |  | 0
Fixture Drain or Trap Size 1 1/4 Inch | [8 empty] | 1 |  |  |  | 0
Fixture Drain or Trap Size 1 1/2 Inch | [8 empty] | 2 |  |  |  | 0
Fixture Drain or Trap Size 2 Inch | [8 empty] | 3 |  |  |  | 0
Fixture Drain or Trap Size 2 1/2 Inch | [8 empty] | 4 |  |  |  | 0
Fixture Drain or Trap Size 3 Inch | [8 empty] | 5 |  |  |  | 0
Fixture Drain or Trap Size 4 Inch | [8 empty] | 6 |  |  |  | 0
0
Note on F29: 4 In/Hr RF for Egypt & Lebanon.
Note on M29: If duplex set is used, the discharge of each pump must be equal to the total demand.
Pipe Data
Print
Options
Back
Back
Go To Head Calculations
Units
S.I
British

## BOOSTER EXPANSION TANK (hidden)
| Booster Expansion Tank |  |  |  |  | PUMP MOTOR POWER P(KW) | MAX. STARTS PER HOUR N
Pump Motor Power (Kw) |  |  |  | Normaly P2 = P1 + 2Bars | 1 | Calculate Power from Pump Input Data
|  |  |  | Normaly Pc = P1 |  | 1 | 120 | 1 | 1
[6 empty] | 2 | 90 | 0 | 2
|  |  |  | Normaly P1 < P2 < H0 |  | 4 | 60 | 0 | 3
[6 empty] | 6 | 50 | 0 | 4
[6 empty] | 8 | 35 | 0 | 5
[6 empty] | 10 | 30 | 0 | 6
[6 empty] | 12 | 25 | 0 | 7
[6 empty] | 14 | 22 | 0 | 8
[6 empty] | 16 | 20 | 0 | 9
1
MAI PLUMBING CALCULATIONS |  | Booster Expansion Tank
Project: |  | Building:
Client: |  | Floor:
Contractor: |  | Axes:
Engineer: |  | Tank No.:
Pump Input Data
Q=Pump Capacity (L / Min) | [5 empty] | cond_p2 | cond_pc
H=Pump Head (Rel. Bar) @ Flow=Q | [5 empty] | 0 | 0
H0=Pump Head (Rel. Bar) @ Flow=0
Pump Motor Power (KW) |  | 0
No. of Pump Starts
Safety Factor for Number of Starts Per Hour (>=1)
Number of Pump Starts Per Hour
Tank Pressures Control
P1=Min. Switch-On Pressure (Rel. Bar) |  | 0 | #VALUE!
P2=Max. Switch-Off Pressure (Rel. Bar)(<=H0)
Pc=Tank Precharge Pressure (Pc<=P1)
Results
Calculated Tank Volume (L) |  | 0
Efficiency of The Pressure Tank (%) |  | 0
Efficient Volume (L) |  | 0
Back
Options
Tank Data
Print

## Dialog_PROJECT_DATA (hidden)
Project Data
OK
Cancel
Project
Client
Contractor
Engineer

## Dialog_option_booster_discharge (hidden)
Options
Cancel
Delete Pump
Open Pump
Save Pump
List of Saved Booster Pump Set Discharges
Reset

## List reference (hidden)
| Booster Discharge | Booster Head | Circulating | Submersible Discharge | Submersible Head | Roof Drains | RW Pipes | Waste Pipes | Vent Pipes | CW & HW Pipes | HWR Pipes | compressed air Pipes | vacuum Pipes | fuel Pipes | CALNCELED(submersible pump disch Pipes) | sump pits | fhc pump | fhc pipes | sprinkler pipes | combined pipes | CO2 pipes | sprinkler distribution | fm-200 nozzles | fm-200 storage | co2 nozzles | CANCELLED(co2 TFS_DSF storage) | CANCELLED(co2 LAS_V storage) | CANCELLED(co2 LAS_A storage) | HVAC CIRCULATING | FANS & AHUS | HWST | Heat Exchanger | Booster Expansion Tank | Noise | EXPansion Tank | CO2 STORAGE | CONDENSATE DRAIN PIPES | REFRIGERANT PIPES | Heating Pipes |  | sheet name
Cell Links | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | BOOSTER PUMP SET HEAD
1 | BPS_A_DISCHARGE |  |  |  | SDP_1_HEAD |  | RW NETWORK NO. dd | WASTE NETWORK NO. DDDD | VENT NETWORK NO. K |  |  |  |  | GAS NETWORK NO. sss | SDP_12_DISCHARGE | [8 empty] | FM-200_SC IN SECURITY OFFICE | [8 empty] | BSTR_TANK_W | [6 empty] | 2 | BOOSTER PUMP SET DISCHARGE
2 | [39 empty] | 3 | HOT WATER CIRCULATING PUMP
3 | [39 empty] | 4 | SUBMERSIBLE PUMP DISCHARGE
4 | [39 empty] | 5 | SUBMERSIBLE PUMP HEAD
5 | [39 empty] | 6 | SUMP PIT
6 | [39 empty] | 7 | RAIN WATER DRAINAGE PIPES
7 | [39 empty] | 8 | WASTE DRAINAGE PIPES_
8 | [39 empty] | 9 | VENT PIPES_
9 | [39 empty] | 10 | COLD & HOT WATER PIPES_
10 | [39 empty] | 11 | HOT WATER RETURN PIPES
11 | [39 empty] | 12 | COMPRESSED AIR PIPES
12 | [39 empty] | 13 | VACUUM AIR PIPES
13 | [39 empty] | 14 | GAS PIPES
14 | [39 empty] | 15 | BOOSTER EXPANSION TANK
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100

## References (hidden)
References
Calculation Sheet | References
Pipulator | ASHRAE, Carrier
Booster Pump Set | ASHRAE, Carrier, Liqui-Trol Catalogue
Booster Expansion Tank | Elbi Catalogue
Hot Water Circulating Pump | ASHRAE, Carrier
Submersible Pump | National Plumbing Code, ASHRAE, Carrier
Sump Pit | National Plumbing Code
Roof Drains | National Plumbing Code
Rain Water Drainage Pipes | National Plumbing Code
Waste Drainage Pipes | National Plumbing Code
Vent Pipes | National Plumbing Code
Cold & Hot Water Pipes | National Plumbing Code, ASHRAE, Carrier
Hot Water Return Pipes | ASHRAE, Carrier
Compressed Air Pipes | CapitoLine
Vacuum Air Pipes | CapitoLine
Gas Pipes | NFPA-54
Back
Print

## MAI Plumbing Calculations
PLUMBING CALCULATIONS
Version 1.7-2014
MAI
Project Data
Main Menu
References
About MAI Plumbing Calculations
Quit

## UNITS CONVERTOR (hidden)
Units Convertor
[5 empty] | 3 | 6 | Length | mm | cm | m | inch | ft
|  |  | 1 | m3/hr |  |  | mm | 1 | 0.1 | 0.001 | 0.03937 | 0.0032808
| From | To | Is equal to |  |  |  | cm | 10 | 1 | 0.01 | 0.3937 | 0.032808
|  |  | 0.27778 | Lps |  |  | m | 1000 | 100 | 1 | 39.3701 | 3.2808
| 3 | 2 |  |  |  |  | inch | 25.4 | 2.54 | 0.0254 | 1 | 0.083333
[7 empty] | ft | 304.8 | 30.48 | 0.3048 | 12 | 1
[7 empty] | Area | mm2 | cm2 | m2 | inch2 | ft2
[7 empty] | mm2 | 1 | 0.01 | 1e-06 | 0.00155 | 1.0764e-05
[7 empty] | cm2 | 100 | 1 | 0.0001 | 0.155 | 0.0010764
[7 empty] | m2 | 1000000 | 10000 | 1 | 1550.0031 | 10.7639
[7 empty] | inch2 | 645.16 | 6.4516 | 0.00064516 | 1 | 0.0069444
[7 empty] | ft2 | 92903.04 | 929.0304 | 0.092903 | 144 | 1
[7 empty] | Volume | mm3 | cm3 | m3 | inch3 | ft3 | Liter | Gallon
[7 empty] | mm3 | 1 | 0.001 | 1e-09 | 6.1024e-05 | 3.5315e-08 | 1e-06 | 2.642e-07
[7 empty] | cm3 | 1000 | 1 | 1e-06 | 0.061024 | 3.5315e-05 | 0.001 | 0.0002642
[7 empty] | m3 | 1000000000 | 1000000 | 1 | 61023.7441 | 35.3147 | 1000 | 264.2008
[7 empty] | inch3 | 16387.064 | 16.3871 | 1.6387e-05 | 1 | 0.0005787 | 0.016387 | 0.0043295
[7 empty] | ft3 | 28316846.592 | 28316.8466 | 0.028317 | 1728 | 1 | 28.3168 | 7.4813
[7 empty] | Liter | 1000000 | 1000 | 0.001 | 61.0237 | 0.035315 | 1 | 0.2642
[7 empty] | Gallon | 3785000 | 3785 | 0.003785 | 230.9749 | 0.13367 | 3.785 | 1
[7 empty] | Mass | Kg | Lb
[7 empty] | Kg | 1 | 2.2046
[7 empty] | Lb | 0.45359 | 1
[7 empty] | Temp. | oC | oF | oK
[7 empty] | oC | 1 |  |  | f=1.8c+32
[7 empty] | oF |  | 1 |  | c=0.55(f-32)
[7 empty] | oK |  |  | 1 | c=k-273.15
[7 empty] | Flow | Cfh | Cfm | Lps | Gpm | Lpm | m3/hr
[7 empty] | Cfh | 1 | 60 | 28.3164 | 448.8729 | 1698.984 | 101.939
[7 empty] | Cfm | 0.016667 | 1 | 0.47194 | 7.4812 | 28.3164 | 1.699
[7 empty] | Lps | 0.035315 | 2.1189 | 1 | 15.852 | 60 | 3.6
[7 empty] | Gpm | 0.0022278 | 0.13367 | 0.063083 | 1 | 3.785 | 0.2271
[7 empty] | Lpm | 0.00058859 | 0.035315 | 0.016667 | 0.2642 | 1 | 0.06
[7 empty] | m3/hr | 0.0098098 | 0.58859 | 0.27778 | 4.4033 | 16.6667 | 1
[7 empty] | Velocity | m/s | ft/s | ft/min
[7 empty] | m/s | 1 | 3.2808 | 196.8504
[7 empty] | ft/s | 0.3048 | 1 | 0.016667
[7 empty] | ft/min | 0.00508 | 60 | 1
[7 empty] | Pressure | bar | mbar | Psi | pa | Kpa | m water | ft water | inch water | mm Hg | inch Hg | atm
[7 empty] | bar | 1 | 1000 | 14.5038 | 100000 | 100 | 10.1972 | 33.4553 | 401.463 | 750.064 | 29.53 | 0.98692
[7 empty] | mbar | 0.001 | 1 | 0.014504 | 100 | 0.1 | 0.010197 | 0.033455 | 0.40146 | 0.75006 | 0.02953 | 0.00098692
[7 empty] | Psi | 0.068947 | 68.9474 | 1 | 6894.7448 | 6.8947 | 0.70307 | 2.3067 | 27.6798 | 51.715 | 2.036 | 0.068046
[7 empty] | pa | 1e-05 | 0.01 | 0.00014504 | 1 | 0.001 | 0.00010197 | 0.00033455 | 0.0040146 | 0.0075006 | 0.0002953 | 9.8692e-06
[7 empty] | Kpa | 0.01 | 10 | 0.14504 | 1000 | 1 | 0.10197 | 0.33455 | 4.0146 | 7.5006 | 0.2953 | 0.0098692
[7 empty] | m water | 0.098066 | 98.0661 | 1.4223 | 9806.6136 | 9.8066 | 1 | 3.2808 | 39.3699 | 73.5559 | 2.8959 | 0.096783
[7 empty] | ft water | 0.029891 | 29.8906 | 0.43353 | 2989.063 | 2.9891 | 0.3048 | 1 | 12 | 22.4199 | 0.88267 | 0.0295
[7 empty] | inch water | 0.0024909 | 2.4909 | 0.036127 | 249.089 | 0.24909 | 0.0254 | 0.083333 | 1 | 1.8683 | 0.073556 | 0.0024583
[7 empty] | mm Hg | 0.0013332 | 1.3332 | 0.019337 | 133.322 | 0.13332 | 0.013595 | 0.044603 | 0.53524 | 1 | 0.03937 | 0.0013158
[7 empty] | inch Hg | 0.033864 | 33.8639 | 0.49115 | 3386.3867 | 3.3864 | 0.34532 | 1.1329 | 13.5951 | 25.4001 | 1 | 0.033421
[7 empty] | atm | 1.0133 | 1013.2534 | 14.696 | 101325.3354 | 101.3253 | 10.3323 | 33.8987 | 406.7837 | 760.0049 | 29.9214 | 1
[7 empty] | Power | Watts | Kw | Kcal/hr | Btu/hr | Ton Ref
[7 empty] | Watts | 1 | 0.001 | 0.85991 | 3.4121 | 0.00028433
[7 empty] | Kw | 1000 | 1 | 859.9143 | 3412.14 | 0.28433
[7 empty] | Kcal/hr | 1.1629 | 0.0011629 | 1 | 3.968 | 0.00033065
[7 empty] | Btu/hr | 0.29307 | 0.00029307 | 0.25202 | 1 | 8.333e-05
[7 empty] | Ton Ref | 3517 | 3.517 | 3024.3186 | 12000.4964 | 1
[7 empty] | Heat Transfer | W / oK m2 | Kcal / Hr oK m2 | Btu / Hr oF ft2
[7 empty] | W / oK m2 | 1 | 0.85991 | 0.17611
[7 empty] | Kcal / Hr oK m2 | 1.1629 | 1 | 0.2048
[7 empty] | Btu / Hr oF ft2 | 5.6783 | 4.8828 | 1
[7 empty] | Linear friction loss | Pa/m | Psi/ft | Psi/100ft | In/100ft | Percent
[7 empty] | Pa/m | 1 | 4.4219e-05 | 0.0044219 | 0.1224 | 0.010197
[7 empty] | Psi/ft | 22614.763 | 1 | 100 | 2767.9849 | 230.6073
[7 empty] | Psi/100ft | 226.1476 | 0.01 | 1 | 27.6798 | 2.3061
[7 empty] | In/100ft | 8.1701 | 0.00036127 | 0.036127 | 1 | 0.083312
[7 empty] | Percent | 98.0661 | 0.0043364 | 0.43364 | 12.003 | 1
Back
Length
Area
Volume
Mass
Temperature
Velocity
Pressure
Power
Flow
Heat transfer
Categories
Convert
Linear Friction Loss

## MECHANICAL (hidden)
MAI Plumbing Calculations
| General | Plumbing
Back