No. people at camp = 150 person.

Avg. water cons. per person/day = 200 L "as per Egyptian code and national plumbing code" for motel.

Total avg. water cons. /day = 30,000 L/day.

Drainage factor = 0.8 – 0.9 % from water consumption (take it 0.8%).

Total avg. drainage /day = 30,000x0.8 = 24,000 L/day.

Total avg. drainage /hr = 24,000/24 = 1000 L

SEPTIC TANK CALCULATION AND RECOMMENDATIONS:-

- The retention time for sewage at septic tank must be between 24hr to 72hr.

- The volume of septic tank shall be not less than 2m3 and another one will be requested if its volume exceed 36m3.

- The depth of septic tank shall be not less than 1.2m and not exceed 1.85m with slope towards inlet 1/10%.

- It is better to construct septic tank with rectangular shape and with two compartments, satisfying the following conditions:-

  - The capacity of the inlet compartment shall have a capacity not less than 1/3 the total tank capacity

  - The ratio between its length and width shall be 2 or 3.

- The distance between septic tank and distribution box of percolating pit shall be not less than 1.5m.

- The level of outlet pipe shall be less than inlet pipe by 5cm.

Form above:-

Assume retention time = 24hr.

Volume of septic tank required = 1000x24 = 24,000 L (24m3).

Dims. of septic tank required = 6x3x1.5m.

PERCOLATING PIT CALCULATION AND RECOMMENDATIONS:-

- You have to identify the absorption rate of soil as it is vary according to its type (is it clay, sand, porous, rock…etc?).

- The diameter of percolating pit shall not be less than 1m.

- The distance between pit and distribution box shall be not less than 1.5m.

- The distance between two percolating pit shall be not less than 3 times its diameter.

- The distance between percolating pit and any beneath building shall be not less than 6m.

- The percolating pit shall be vented with pipe not less than 10cm.

- The bottom level of percolating pit shall be above level underground water reservoir by min. 2m.

Form above:-

Assume soil is sandy with absorption rate = 120 L/day/m2.

The effective absorption area required = 24,000/120 = 200m2.